## Pivot
|  | Deferred | Insured | Def Maint | Replacement | Estimated
Facility | Area (sf) | Maintenance | Bldg Cost | per SF | Cost/sqft | Replacement Cost | FCI |  |  |  | THIS IS A SUMMARY PIVOT TABLE OF THE TAB "DEFICIENCY SUMMARY"
Emma L Johnston Southside Family Resource Center | 4200 | 334100 | 416326 | 79.5476 | 300 | 1260000 | 0.26516
Transportation Department | 7300 | 278850 | 246279 | 38.1986 | 250 | 1825000 | 0.15279
Eastside Family Resource Center | 10000 | 410250 | 443000 | 41.025 | 265.75 | 2657500 | 0.15437
Westside Family Resource Center | 3700 | 223500 | 735750 | 60.4054 | 300 | 1110000 | 0.20135
DeFrancisco Eastwood Community Center | 12000 | 572000 | 913457 | 47.6667 | 350 | 4200000 | 0.13619
LaFayette Head Start | 4740 | 119300 | 270951 | 25.1688 | 300 | 1422000 | 0.083896
County South Family Resource Center | 3000 | 51750 | 302104 | 17.25 | 300 | 900000 | 0.0575
Sumner Head Start & Big Brothers Big Sisters | 33000 | 892750 | 9046685 | 27.053 | 500 | 16500000 | 0.054106
Merrick Head Start | 43400 | 958800 | 4539999 | 22.0922 | 500 | 21700000 | 0.044184
717 Erie Boulevard West | 9400 | 67750 | 1236069 | 7.2074 | 250 | 2350000 | 0.02883
| 130740 | 3909050 | 18150620 | 29.8994 |  | 53924500
|  |  |  | 35.9558 | 0.072491
Sum of Total Cost | Column Labels
Row Labels | Electrical | Envelope | FireSprinkler | HVAC | Interior | Miscellaneous | Plumbing | Security | Site | FireAlarm | Grand Total
717 Erie Boulevard West |  | 11000 |  | 45000 |  | 750 | 11000 |  |  |  | 67750
County South Family Resource Center |  | 12500 |  | 23000 | 7500 | 1500 | 6750 |  |  | 500 | 51750
DeFrancisco Eastwood Community Center |  | 186000 | 5000 | 330500 | 7500 | 1000 | 27500 |  | 14500 |  | 572000
Eastside Family Resource Center | 52500 | 21500 |  | 228250 |  | 11500 | 57500 |  | 39000 |  | 410250
Emma L Johnston Southside Family Resource Center | 12600 | 123000 |  | 50500 | 60000 | 1500 | 17000 | 0 | 69500 |  | 334100
LaFayette Head Start | 15350 | 2500 | 14000 | 47950 | 1500 | 1500 | 15500 |  | 21000 |  | 119300
Merrick Head Start | 22500 | 299900 |  | 584000 |  | 12400 | 24000 |  | 16000 |  | 958800
Sumner Head Start & Big Brothers Big Sisters | 22000 | 491400 |  | 248450 | 200 | 34400 | 71300 |  | 25000 |  | 892750
Transportation Department | 500 | 52000 |  | 159950 | 1000 | 500 | 39500 |  | 25400 |  | 278850
Westside Family Resource Center | 10000 | 90000 |  | 98000 | 2000 | 1500 | 8500 |  | 13500 |  | 223500
Grand Total | 135450 | 1289800 | 19000 | 1815600 | 79700 | 66550 | 278550 | 0 | 223900 | 500 | 3909050

## Deficiency Summary
|  |  |  | THIS IS THE DATA ENTRY PAGE FROM THE CONDITIONS ASSESSMENT DOCUMENT WHICH CONTAINS THE DEFICIENCY, RECOMMENDATION SUMMARY, PRIORITIZATION, COSTS AND RECOMMENDED ACTION YEAR. THIS IS INTENDED TO BE A WORKING DOC TO TRACK AND MANAGE THE FACILITIES PROJECTS. REFER TO THE "HOW TO USE THIS SPREADSHEET" TAB FOR INSTRUCTIONS | [19 empty] | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year | Year
[5 empty] | Tie assets to this list and relate equipment type to its anticipated life expectancy | [18 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
Deficiency # | Facility | Deficiency Type | Deficiency Subtype | Recommendation Summary | Specific Asset # (if applicable) | Type of Equipment | Age Verified (Yes/No) | Year of Install or Manufacture Date | Effective Age (year) | Median Life Expectancy (years) | Remaining Useful Life (yr) | Likelihood of Failure (1=Low, 5=High) | Impact of Failure (1=Low, 5=High) | Program Factor (1=None, 5=High) | Weighted Priority | Quantity | Unit | Unit Cost | Total Cost | Cost Source | Complete? Y/N | Recommended Action Year | Funding Source | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | Beyond | Comments
| Eastside Family Resource Center | HVAC | Heating | Replace legacy and supplemental sidearm boiler system. Primary boiler at end of life. |  |  | YES | 1977 | 47 | 35 | -12 | 4 | 5 | 4 | 28 | 1 | ls | 150000 | 150000 | PGPC | NO | 2025 |  | 2: 150000
| Westside Family Resource Center | Envelope | Substructure | Perform investigation of 1st floor structural framing system that is failing and correct issues with pitched floor and racking windows and doors in area. |  |  |  |  | 2024 |  | N/A | 5 | 4 | 3 | 26 | 1 | ls | 30000 | 30000 | PGPC | NO | 2025 |  | 2: 30000
| Emma L Johnston Southside Family Resource Center | Site | Topology and Drainage | Improve site drainage on east side of property to prevent water infiltration into basement |  |  |  |  | 2024 |  | N/A | 5 | 4 | 3 | 26 | 1 | ls | 20000 | 20000 | PGPC | NO | 2025 |  | 2: 20000
| Transportation Department | Site | Paving and Curbing | Improve grading at driveway apron to mitigate vehicle damage |  |  |  |  | 2024 |  | N/A | 5 | 4 | 3 | 26 | 1 | ls | 20000 | 20000 | PGPC | NO | 2030 |  | 7: 20000
| Westside Family Resource Center | Envelope | Substructure | Mitigate moisture infiltration into the basement |  |  |  |  | 2024 |  | N/A | 5 | 4 | 3 | 26 | 1 | ls | 10000 | 10000 | PGPC | NO | 2025 |  | 2: 10000
| Emma L Johnston Southside Family Resource Center | Plumbing | Interior Storm drainage | Provide sump pump to remove water infiltration and flooding |  |  |  |  | 2024 |  | N/A | 5 | 4 | 3 | 26 | 1 | ls | 7500 | 7500 | PGPC | NO | 2026 |  | 3: 7500
| DeFrancisco Eastwood Community Center | Envelope | Façade | Hose tower and building façade restoration |  |  |  |  | 2024 |  | N/A | 5 | 4 | 3 | 26 | 0 | ea | 400000 | 0 | PGPC | NO | 2024 |  | 1: 0
| Westside Family Resource Center | Site | Topology and Drainage | Regrade north side of property to mitigate water infiltration into building |  | STORMWATER MANAGEMENT |  |  | 2024 |  | N/A | 5 | 4 | 2 | 24 | 1 | ls | 6000 | 6000 | PGPC | NO | 2025 |  | 2: 6000
| Emma L Johnston Southside Family Resource Center | Envelope | Substructure | Investigate and perform stone foundation repairs |  |  |  |  | 2024 |  | N/A | 5 | 3 | 5 | 22.5 | 1 | ea | 40000 | 40000 | PGPC | NO | 2025 |  | 2: 40000
| Sumner Head Start & Big Brothers Big Sisters | Envelope | Roofing | Replace roof - roofing near end of life. Surface ponding present. Include adding drainage/roof cants at elevator overrun, extending condensate lines closer to roof drains, and removing abandoned roof vents. |  | ROOF |  | 1997 | 27 | 30 | 3 | 4 | 4 | 4 | 22.4 | 26000 | ft2 | 14 | 364000 | PEACE | NO | 2028 |  | 5: 364000
| DeFrancisco Eastwood Community Center | Envelope | Roofing | Roof at end of life. Replace roofing. |  |  |  |  | 2024 |  | N/A | 4 | 4 | 4 | 22.4 | 4000 | ft2 | 14 | 56000 | PGPC | NO | 2024 |  | 1: 56000
| Emma L Johnston Southside Family Resource Center | HVAC | Heating | Replace existing forced air furnace at end of life. Unit in attic serves 2nd fl community rm. | 101007 | FURNACE | YES | 1993 | 31 | 18 | -13 | 4 | 4 | 4 | 22.4 | 1 | ls | 8500 | 8500 | PGPC | NO | 2025 |  | 2: 8500
| Emma L Johnston Southside Family Resource Center | HVAC | Heating | Replace existing forced air furnace at end of life. Unit in basement. Serves 1st floor. | 101004 | FURNACE | YES | 1993 | 31 | 18 | -13 | 4 | 4 | 4 | 22.4 | 1 | ls | 8500 | 8500 | PGPC | NO | 2025 |  | 2: 8500
| Eastside Family Resource Center | Plumbing | Interior Storm drainage | Investigate basement flooding issue due to potential flow restriction from roots in drain line |  |  | NO | 1944 | 80 | 70 | -10 | 4 | 4 | 4 | 22.4 | 1 | ea | 5000 | 5000 | PGPC | NO | 2025 |  | 2: 5000
J.7.d | LaFayette Head Start | FireSprinkler | Main Service | Replace Fire Service Pumps, raise on platform to prevent damage from site flooding | 101088 | PUMP - FIRE | NO | 2017 | 7 | 20 | 13 | 4 | 5 | 1 | 22 | 2 | ea | 7000 | 14000 | PGPC | NO | 2026 |  | 3: 14000
| 717 Erie Boulevard West | HVAC | Heating | Replace rooftop air handling units, total of 3 at end of life |  | AIR CONDITIONER | NO | 2012 | 12 | 15 | 3 | 3 | 5 | 4 | 21 | 3 | ea | 10000 | 30000 | PGPC | NO | 2027 |  | 4: 30000
| DeFrancisco Eastwood Community Center | HVAC | Heating | Replace natural gas duct furnace for AHU-1 (1st floor heat) | 101080 | FURNACE | YES | 2003 | 21 | 18 | -3 | 3 | 5 | 4 | 21 | 1 | ls | 10000 | 10000 | PGPC | NO | 2024 |  | 1: 10000
| DeFrancisco Eastwood Community Center | HVAC | Heating | Replace natural gas duct furnace for AHU-2 (2nd floor heat) | 101022 | FURNACE | YES | 2003 | 21 | 18 | -3 | 3 | 5 | 4 | 21 | 1 | ls | 10000 | 10000 | PGPC | NO | 2024 |  | 1: 10000
| Westside Family Resource Center | Envelope | Substructure | Investigate structural integrity of existing foundation system and provide repairs as needed. |  |  |  |  | 2024 |  | N/A | 4 | 4 | 3 | 20.8 | 1 | ls | 10000 | 10000 | PGPC | NO | 2025 |  | 2: 10000
| Westside Family Resource Center | HVAC | Heating | Replace existing boiler that is near end of life, add chemical treatment | 101022 |  |  |  | 2024 |  | N/A | 3 | 5 | 3 | 19.5 | 1 | ls | 20000 | 20000 | PGPC | NO | 2028 |  | 5: 20000
| Westside Family Resource Center | Envelope | Substructure | Seal up openings in building envelope at basement level. Repair or replace deteriorating sill plates, framing, etc. |  | BOILER, NATURAL GAS |  |  | 2024 |  | N/A | 5 | 3 | 3 | 19.5 | 1 | ls | 15000 | 15000 | PGPC | NO | 2025 |  | 2: 15000
| Merrick Head Start | HVAC | Heating | Replace failed steam valve on convector in gymnasium |  |  | NO | 2010 | 14 | 10 | -4 | 5 | 3 | 3 | 19.5 | 1 | ea | 500 | 500 | PGPC | NO | 2025 |  | 2: 500
| Transportation Department | HVAC | Heating | Replace natural gas boiler. Unit has surpassed service life expectancy. | 101009 | BOILER, NATURAL GAS | YES | 1999 | 25 | 24 | -1 | 4 | 4 | 2 | 19.2 | 1 | ls | 27200 | 27200 | RSMeans | NO | 2026 |  | 3: 27200
| Emma L Johnston Southside Family Resource Center | HVAC | Heating | Replace existing forced air furnace at end of life. Unit in attic serves 2nd fl apartment. | 101008 | FURNACE | YES | 1993 | 31 | 18 | -13 | 4 | 4 | 2 | 19.2 | 1 | ls | 8500 | 8500 | PGPC | NO | 2025 |  | 2: 8500
| Transportation Department | HVAC | Heating | Replace heating system steam and condensate piping and terminal units which are at end of life. |  |  | NO | 1960 | 64 | 50 | -14 | 3 | 4 | 5 | 18 | 1 | ls | 85000 | 85000 | PGPC | NO | 2030 |  | 7: 85000
| County South Family Resource Center | HVAC | Heating | Replace gas forced air furnace - Attic south |  | FURNACE | YES | 1994 | 30 | 18 | -12 | 4 | 3 | 5 | 18 | 1 | ea | 7500 | 7500 | PGPC | NO | 2025 |  | 2: 7500
| County South Family Resource Center | HVAC | Heating | Replace gas forced air furnace - Attic north |  | FURNACE | YES | 1994 | 30 | 18 | -12 | 4 | 3 | 5 | 18 | 1 | ea | 7500 | 7500 | PGPC | NO | 2025 |  | 2: 7500
| County South Family Resource Center | Plumbing | Domestic HW Heating System | Replace hot water heater - basement center |  | DOMESTIC HOT WATER HEATER GAS | YES | 1994 | 30 | 12 | -18 | 5 | 3 | 2 | 18 | 1 | ea | 2000 | 2000 | RSMeans | NO | 2025 |  | 2: 2000
| County South Family Resource Center | HVAC | Heating | Repair failed flue vents |  | FURNACE |  |  | 2024 |  | N/A | 5 | 3 | 2 | 18 | 1 | ls | 1000 | 1000 | PGPC | NO | 2025 |  | 2: 1000
| Emma L Johnston Southside Family Resource Center | Plumbing | Domestic HW Heating System | Domestic water heater replacement - Right hand unit, serves 1st floor | 101003 | DOMESTIC HOT WATER HEATER GAS | YES | 2010 | 14 | 12 | -2 | 4 | 3 | 4 | 16.8 | 1 | ls | 3000 | 3000 | PGPC | NO | 2024 |  | 1: 3000
| County South Family Resource Center | FireAlarm | Devices | Install CO detector for the attic space in the vicinity of the gas fired appliances (Code) |  |  |  |  | 2024 |  | N/A | 5 | 3 | 1 | 16.5 | 1 | ea | 500 | 500 | PGPC | NO | 2025 |  | 2: 500
| Merrick Head Start | HVAC | Ventilating | Replace steam unit ventilators |  | HEATING AND VENTILATION UNITS | YES | 1955 | 69 | 25 | -44 | 3 | 4 | 3 | 15.6 | 17 | ea | 15000 | 255000 | RSMeans | NO | 2027 |  | 4: 255000
3.f.2 | Merrick Head Start | Envelope | Roofing | Replace roof - roofing near end of life |  |  |  | 2000 | 24 | 30 | 6 | 4 | 3 | 3 | 15.6 | 16500 | ft2 | 13 | 214500 | PGPC | NO | 2030 |  | 7: 214500
| Westside Family Resource Center | Envelope | Roofing | Address roof pitch, install gutter system ncluding downspouts, underdrains |  |  |  |  | 2024 |  | N/A | 4 | 3 | 3 | 15.6 | 1 | ls | 25000 | 25000 | PGPC | NO | 2025 |  | 2: 25000
E.1.d.4 | LaFayette Head Start | HVAC | Air Conditioning | Replace R-22 A/C system for Gym | 101135 | CONDENSER FOR HVAC | YES | 2002 | 22 | 20 | -2 | 4 | 3 | 3 | 15.6 | 1 | ea | 20000 | 20000 | PGPC | NO | 2026 |  | 3: 20000
| Eastside Family Resource Center | HVAC | Heating | Replace terminal heating units |  |  | NO | 1960 | 64 | 50 | -14 | 3 | 4 | 3 | 15.6 | 1 | ls | 15000 | 15000 | PGPC | NO | 2028 |  | 5: 15000
| Emma L Johnston Southside Family Resource Center | Plumbing | Domestic HW Heating System | Domestic water heater replacement - Left hand unit, serves 2nd fl apt.#1 | 101001 | DOMESTIC HOT WATER HEATER GAS | YES | 1998 | 26 | 12 | -14 | 4 | 3 | 3 | 15.6 | 1 | ls | 3000 | 3000 | PGPC | NO | 2024 |  | 1: 3000 |  | need to verify age of roof and date of install
| Emma L Johnston Southside Family Resource Center | Plumbing | Domestic HW Heating System | Domestic water heater replacement - center unit, serves 2nd fl apt.#2 | 101002 | DOMESTIC HOT WATER HEATER GAS | YES | 1998 | 26 | 12 | -14 | 4 | 3 | 3 | 15.6 | 1 | ls | 3000 | 3000 | PGPC | NO | 2024 |  | 1: 3000
| DeFrancisco Eastwood Community Center | HVAC | Ventilating | Replace or rebuild air handling unit AHU-2 serving 2nd floor heating/cooling/ventilation | 101123 | AIR CONDITIONER | YES | 2003 | 21 | 30 | 9 | 2 | 5 | 5 | 15 | 1 | ls | 47600 | 47600 | PGPC | NO | 2033 |  | 10: 47600 |  | If fan fails, this would limit cooking operations for facility
| DeFrancisco Eastwood Community Center | HVAC | Ventilating | Replace or rebuild air handling unit AHU-1 serving 1st floor heating/cooling/ventilation |  | AIR CONDITIONER | YES | 2003 | 21 | 30 | 9 | 2 | 5 | 5 | 15 | 1 | ls | 39200 | 39200 | PGPC | NO | 2033 |  | 10: 39200
| LaFayette Head Start | Plumbing | Domestic Water Supply | Replace submersible well pump at end of service life, 1/2HP 17 gpm (approx) |  | PUMP - BOOSTER | NO | 2016 | 8 | 15 | 7 | 2 | 5 | 5 | 15 | 1 | ea | 2500 | 2500 | PGPC | NO | 2031 |  | 8: 2500
| DeFrancisco Eastwood Community Center | Interior | Flooring | Replace mezzanine level flooring adjacent to the garage door (north side of building) |  |  |  |  | 2024 |  | N/A | 4 | 3 | 2 | 14.4 | 1 | ea | 4000 | 4000 | PGPC | NO | 2024 |  | 1: 4000
| County South Family Resource Center | Plumbing | Domestic HW Heating System | Replace hot water heater - basement left |  | DOMESTIC HOT WATER HEATER GAS | YES | 2008 | 16 | 12 | -4 | 4 | 3 | 2 | 14.4 | 1 | ea | 2000 | 2000 | RSMeans | NO | 2025 |  | 2: 2000
| DeFrancisco Eastwood Community Center | HVAC | Ventilating | Kitchen range hood fan not operating. Replace range hood. |  |  | NO | 2010 | 14 | 15 | 1 | 5 | 2 | 4 | 14 | 1 | ls | 1200 | 1200 | PGPC | NO | 2025 |  | 2: 1200 |  | testing of BFPV will require building water shutdown and outage which means no restrooms. Potential program issue. Need owner input.
| Sumner Head Start & Big Brothers Big Sisters | HVAC | Air Conditioning | Replace rooftop air handling unit at end of life - RTU1. Serves 2nd Floor west classrooms. | 101044 | AIR CONDITIONER | YES | 2004 | 20 | 25 | 5 | 3 | 3 | 5 | 13.5 | 1 | ea | 32000 | 32000 | PGPC | NO | 2029 |  | 6: 32000
| Sumner Head Start & Big Brothers Big Sisters | HVAC | Air Conditioning | Replace rooftop air handling unit at end of life - RTU2. Serves 2nd Floor east classrooms. | 101045 | AIR CONDITIONER | YES | 2004 | 20 | 25 | 5 | 3 | 3 | 5 | 13.5 | 1 | ea | 32000 | 32000 | PGPC | NO | 2029 |  | 6: 32000
| Sumner Head Start & Big Brothers Big Sisters | HVAC | Air Conditioning | Replace rooftop air handling unit at end of life - RTU3. Serves 1st Floor east classrooms and building main entry lobby | 101046 | AIR CONDITIONER | YES | 2004 | 20 | 25 | 5 | 3 | 3 | 5 | 13.5 | 1 | ea | 32000 | 32000 | PGPC | NO | 2029 |  | 6: 32000
| Sumner Head Start & Big Brothers Big Sisters | HVAC | Air Conditioning | Replace rooftop air handling unit at end of life - RTU4. Serves 1st Floor west classrooms. | 101047 | AIR CONDITIONER | YES | 2004 | 20 | 25 | 5 | 3 | 3 | 5 | 13.5 | 1 | ea | 32000 | 32000 | PGPC | NO | 2029 |  | 6: 32000
| County South Family Resource Center | HVAC | Heating | Replace gas forced air furnace - basement |  | FURNACE | YES | 2001 | 23 | 18 | -5 | 3 | 3 | 5 | 13.5 | 1 | ea | 6000 | 6000 | PGPC | NO | 2026 |  | 3: 6000
| Westside Family Resource Center | HVAC | Heating | Replace south end ductwork through crawlspace believed to be compromised |  |  |  |  | 2024 |  | N/A | 4 | 3 | 1 | 13.2 | 1 | ls | 10000 | 10000 | PGPC | NO | 2028 |  | 5: 10000
| Transportation Department | HVAC | Capital Improvement | Provide service isolation valves for terminal equipment (radiators) to allow service without entire heating system shutdown |  | FLUID LOOP |  | 1960 | 64 | 50 | -14 | 3 | 4 | 1 | 13.2 | 7 | ea | 750 | 5250 | PGPC | NO | 2024 |  | 1: 5250
| Sumner Head Start & Big Brothers Big Sisters | Envelope | Maintenance | Inspect chimney internals for structural integrity. Evidence of deterioration and water infiltration observed at base of chimney in boiler room. |  |  | YES | 1954 | 70 | 65 | -5 | 2 | 5 | 3 | 13 | 1 | ls | 10000 | 10000 | PGPC | NO | 2026 |  | 3: 10000
| Eastside Family Resource Center | HVAC | Heating | Investigate solutions to cold temps and remediate poor insulation and/or equipment performance issues |  |  |  |  | 2024 |  | N/A | 4 | 2 | 5 | 12 | 1 | ea | 40000 | 40000 | PGPC | NO | 2026 |  | 3: 40000
| Emma L Johnston Southside Family Resource Center | Site | Flatwork / Sidewalks | Extensive sidewalk repair |  |  |  |  | 2024 |  | N/A | 5 | 2 | 2 | 12 | 60 | ea | 500 | 30000 | PGPC | NO | 2030 |  | 7: 30000
| Eastside Family Resource Center | Site | Topology and Drainage | Install rainwater gutters on north side of roof and connect to downspout and site drainage system to reduce water infiltration |  |  |  |  | 2024 |  | N/A | 5 | 2 | 2 | 12 | 1 | ea | 15000 | 15000 | PGPC | NO | 2025 |  | 2: 15000
| County South Family Resource Center | Envelope | Roofing | Replace roof gutter system | [6 empty] | N/A | 5 | 2 | 2 | 12 | 1 | ea | 8000 | 8000 | PGPC | NO | 2027 |  | 4: 8000
| Emma L Johnston Southside Family Resource Center | Envelope | Façade | Envelope repair west side |  |  |  |  | 2024 |  | N/A | 5 | 2 | 2 | 12 | 1 | ls | 3000 | 3000 | PGPC | NO | 2029 |  | 6: 3000
| Transportation Department | Site | Flatwork / Sidewalks | Replace deteriorated concrete flags from City sidewalk to the south entry door |  |  |  |  | 2024 |  | N/A | 5 | 2 | 2 | 12 | 6 | ea | 400 | 2400 | PGPC | NO | 2027 |  | 4: 2400
| Sumner Head Start & Big Brothers Big Sisters | Envelope | Windows | Replace remaining windows that have not been replaced from 2016 window replacements. 40 windows on 1st floor and 34 on 2nd floor need replacement. |  | WINDOW |  |  | 2024 |  | N/A | 3 | 3 | 3 | 11.7 | 74 | ls | 1100 | 81400 | PGPC | NO | 2026 |  | 3: 81400
| Westside Family Resource Center | HVAC | Heating | Replace / update existing terminal units (fin tube, convectors) |  |  |  |  | 2024 |  | N/A | 3 | 3 | 3 | 11.7 | 1 | ls | 15000 | 15000 | PGPC | NO | 2028 |  | 5: 15000
| Sumner Head Start & Big Brothers Big Sisters | HVAC | Air Conditioning | Clean debris off RTU condensing unit coil fin surfaces to mitigate premature failure. Condensers were mostly plugged. |  | AIR CONDITIONER |  |  | 2024 |  | N/A | 3 | 3 | 3 | 11.7 | 4 | ea | 200 | 800 | PGPC | NO | 2025 |  | 2: 800
| DeFrancisco Eastwood Community Center | HVAC | Air Conditioning | Replace building air conditioning condensing unit, RCU-2, for AHU-2 (2nd floor) - 8 ton. Need to replace indoor evaporator coil with compliant refrigerant. | 101128 | CONDENSER FOR HVAC | YES | 2003 | 21 | 15 | -6 | 4 | 2 | 4 | 11.2 | 1 | ls | 54000 | 54000 | PGPC | NO | 2027 |  | 4: 54000
| DeFrancisco Eastwood Community Center | HVAC | Air Conditioning | Replace building air conditioning condensing unit, RCU-1, for AHU-1 (1st floor) - 7.5 ton. Need to replace indoor evaporator coil with compliant refrigerant. | 101129 | CONDENSER FOR HVAC | YES | 2003 | 21 | 15 | -6 | 4 | 2 | 4 | 11.2 | 1 | ls | 48000 | 48000 | PGPC | NO | 2027 |  | 4: 48000
| Transportation Department | Envelope | Roofing | Repair and replace exterior gutters and provision of (2) additional downspouts with underdrains to below grade, including heat trace ice meltning system to protect gutters from winter damage. |  |  |  |  | 2024 |  | N/A | 5 | 2 | 1 | 11 | 1 | ls | 12000 | 12000 | PGPC | NO | 2030 |  | 7: 12000
| Sumner Head Start & Big Brothers Big Sisters | Envelope | Roofing | Provide saftey railing along east high roof edge by rooftop unit, RTU3, located close to roof edge to comply with OSHA regulations. |  |  |  |  | 2024 |  | N/A | 2 | 5 | 1 | 11 | 1 | ls | 10000 | 10000 | PGPC | NO | 2025 |  | 2: 10000
| 717 Erie Boulevard West | Envelope | Roofing | Repair water infiltration issue at northwest corner of roof and wall assembly to prevent water mitigation and moisture issues |  |  |  |  | 2024 |  | N/A | 5 | 2 | 1 | 11 | 1 | ea | 5000 | 5000 | PGPC | NO | 2024 |  | 1: 5000
| LaFayette Head Start | Envelope | Façade | Upper front eave repair |  |  |  |  | 2024 |  | N/A | 5 | 2 | 1 | 11 | 1 | ea | 2500 | 2500 | PGPC | NO | 2030 |  | 7: 2500
4.a | LaFayette Head Start | Site | Flatwork / Sidewalks | Replace concrete Flags |  |  |  |  | 2024 |  | N/A | 5 | 2 | 1 | 11 | 2 | ea | 500 | 1000 | PGPC | NO | 2026 |  | 3: 1000
| Sumner Head Start & Big Brothers Big Sisters | Envelope | Windows | Provide screens for gymnaisum hopper windows |  |  |  |  | 2024 |  | N/A | 5 | 2 | 1 | 11 | 2 | ea | 500 | 1000 | PGPC | NO | 2025 |  | 2: 1000
| Emma L Johnston Southside Family Resource Center | Interior | Paint | Full interior paint |  |  |  |  | 2024 |  | N/A | 3 | 3 | 2 | 10.8 | 1 | ea | 40000 | 40000 | PGPC | NO | 2030 |  | 7: 40000
| Emma L Johnston Southside Family Resource Center | Envelope | Roofing | Replace roofing at end of life. |  |  | NO | 2018 | 6 | 10 | 4 | 3 | 3 | 2 | 10.8 | 1 | ea | 20000 | 20000 | PGPC | NO | 2028 |  | 5: 20000
| Emma L Johnston Southside Family Resource Center | Interior | Flooring | Replace end of life flooring |  |  |  |  | 2024 |  | N/A | 3 | 3 | 2 | 10.8 | 1 | ea | 20000 | 20000 | PGPC | NO | 2030 |  | 7: 20000
| Sumner Head Start & Big Brothers Big Sisters | HVAC | Ventilating | Replace bathroom exhaust fan, EF-2, on roof at end of life. |  | EXHAUST FAN | YES | 2004 | 20 | 25 | 5 | 3 | 3 | 2 | 10.8 | 1 | ea | 4000 | 4000 | PGPC | NO | 2029 |  | 6: 4000
| Transportation Department | Plumbing | Domestic HW Heating System | Replace water heater | 101010 | DOMESTIC HOT WATER HEATER GAS |  |  | 2024 |  | N/A | 3 | 3 | 2 | 10.8 | 1 | ls | 4000 | 4000 | PGPC | NO | 2029 |  | 6: 4000
| Westside Family Resource Center | Plumbing | Interior Sanitary Drainage | Install backwater valve to mitigate sewer backups, replace floor drain and grate and install cap on open pipe |  |  |  |  | 2024 |  | N/A | 3 | 3 | 2 | 10.8 | 1 | ls | 3500 | 3500 | PGPC | NO | 2025 |  | 2: 3500
| County South Family Resource Center | Plumbing | Domestic HW Heating System | Replace hot water heater - basement right |  | DOMESTIC HOT WATER HEATER GAS | YES | 2013 | 11 | 12 | 1 | 3 | 3 | 2 | 10.8 | 1 | ea | 2000 | 2000 | RSMeans | NO | 2025 |  | 2: 2000
| Eastside Family Resource Center | Electrical | Capital Improvement | Install generator for standby power to preserve refrigerated goods and community access |  | GENERATOR |  |  | 2024 |  | N/A | 2 | 4 | 3 | 10.4 | 1 | ea | 25000 | 25000 | PGPC | NO | 2029 |  | 6: 25000
| Sumner Head Start & Big Brothers Big Sisters | Plumbing | Domestic HW Heating System | Replace domestic water heater for building |  | DOMESTIC HOT WATER HEATER GAS | NO | 2014 | 10 | 15 | 5 | 4 | 2 | 3 | 10.4 | 1 | ea | 20000 | 20000 | PGPC | NO | 2034 |  | 11: 20000
| Sumner Head Start & Big Brothers Big Sisters | Electrical | Site Lighting | Improve site lighting for north parking lot. Insufficient illumination observed. |  |  |  |  | 2024 |  | N/A | 4 | 2 | 3 | 10.4 | 1 | ls | 20000 | 20000 | PGPC | NO | 2026 |  | 3: 20000
| Sumner Head Start & Big Brothers Big Sisters | Site | Paving and Curbing | North parking lot in poor condition. Repair cracking and re-stripe lot. |  |  |  |  | 2024 |  | N/A | 4 | 2 | 3 | 10.4 | 20000 | sf | 1 | 20000 | PGPC | NO | 2026 |  | 3: 20000
| Emma L Johnston Southside Family Resource Center | Site | Paving and Curbing | Repave parking lot |  |  |  |  | 2024 |  | N/A | 4 | 2 | 3 | 10.4 | 4500 | sf | 4 | 18000 | PGPC | NO | 2030 |  | 7: 18000
| DeFrancisco Eastwood Community Center | Plumbing | Domestic HW Heating System | Replace DHW tank that is nearing end of life | 101121 | DOMESTIC HOT WATER HEATER ELECTRIC | YES | 2015 | 9 | 12 | 3 | 2 | 4 | 3 | 10.4 | 1 | ls | 5000 | 5000 | PGPC | NO | 2027 |  | 4: 5000
| DeFrancisco Eastwood Community Center | FireSprinkler | Capital Improvement | Provide 5kW electric heater for garage to protect wet pipe sprinkler system |  | DOMESTIC HOT WATER HEATER ELECTRIC |  |  | 2024 |  | N/A | 2 | 4 | 3 | 10.4 | 1 | ls | 5000 | 5000 | PGPC | NO | 2025 |  | 2: 5000
| Westside Family Resource Center | Plumbing | Domestic HW Heating System | Replace Domestic HW heater that has reached end of life | 101021 | DOMESTIC HOT WATER HEATER GAS |  |  | 2024 |  | N/A | 4 | 2 | 3 | 10.4 | 1 | ls | 3000 | 3000 | PGPC | NO | 2025 |  | 2: 3000
| Sumner Head Start & Big Brothers Big Sisters | Electrical | Site Lighting | Southwest entry canopy lights appear to be broken. Replace entry lights. |  |  |  |  | 2024 |  | N/A | 4 | 2 | 3 | 10.4 | 1 | ls | 2000 | 2000 | PGPC | NO | 2026 |  | 3: 2000
| Emma L Johnston Southside Family Resource Center | Envelope | Façade | Investigate and perform misc brick masonry repairs |  |  |  |  | 2024 |  | N/A | 3 | 3 | 1 | 9.9 | 1 | ea | 25000 | 25000 | PGPC | NO | 2030 |  | 7: 25000
| Eastside Family Resource Center | Plumbing | Domestic HW Heating System | Test, abate and replace all original pipe insulation |  |  |  |  | 2024 |  | N/A | 3 | 3 | 1 | 9.9 | 1 | ea | 20000 | 20000 | PGPC | NO | 2027 |  | 4: 20000
| Eastside Family Resource Center | Envelope | Façade | Paint Exposed CMU |  |  |  |  | 2024 |  | N/A | 3 | 3 | 1 | 9.9 | 1 | ea | 20000 | 20000 | PGPC | NO | 2030 |  | 7: 20000
| Transportation Department | Envelope | Other | Investigate and provide proper stormwater management at east end of property to protect masonry structure and joints from degradation |  | STORMWATER MANAGEMENT |  |  | 2024 |  | N/A | 3 | 3 | 1 | 9.9 | 1 | ls | 20000 | 20000 | PGPC | NO | 2030 |  | 7: 20000
| DeFrancisco Eastwood Community Center | HVAC | Ventilating | Replace 1st floor restroom exhaust fan due to age. |  |  | NO | 2000 | 24 | 25 | 1 | 3 | 3 | 1 | 9.9 | 1 | ls | 1000 | 1000 | PGPC | NO | 2025 |  | 2: 1000
| Sumner Head Start & Big Brothers Big Sisters | Plumbing | Domestic Water Supply | Blow down and inspect storage tank for corrosion |  |  |  |  | 2024 |  | N/A | 3 | 3 | 1 | 9.9 | 1 | ea | 1000 | 1000 | PGPC | NO | 2025 |  | 2: 1000
| DeFrancisco Eastwood Community Center | Envelope | Windows | Window replacements - replace all windows |  |  |  |  | 2024 |  | N/A | 4 | 2 | 2 | 9.6 | 60 | ea | 2000 | 120000 | PGPC | NO | 2032 |  | 9: 120000
| Emma L Johnston Southside Family Resource Center | Envelope | Roofing | Replace roof assembly, approx 2000 sqft. Including soffit, fascia, gutters, downspouts |  |  |  |  | 2024 |  | N/A | 4 | 2 | 2 | 9.6 | 1 | ls | 20000 | 20000 | PGPC | NO | 2030 |  | 7: 20000
| Eastside Family Resource Center | Site | Other | Replace existing west end egress deck with more durable means |  |  |  |  | 2024 |  | N/A | 4 | 2 | 2 | 9.6 | 1 | ea | 15000 | 15000 | PGPC | NO | 2025 |  | 2: 15000
| Merrick Head Start | HVAC | Ventilating | Plan to replace old north gym H&V unit system in near future. Replace in kind or provide modern heating & cooling system. |  | HEATING AND VENTILATION UNITS | NO | 1955 | 69 | 40 | -29 | 4 | 2 | 2 | 9.6 | 1 | ea | 15000 | 15000 | PGPC | NO | 2030 |  | 7: 15000
| Sumner Head Start & Big Brothers Big Sisters | Plumbing | Domestic HW Heating System | Replace domestic water heater for kitchen |  | DOMESTIC HOT WATER HEATER GAS | YES | 2010 | 14 | 15 | 1 | 4 | 2 | 2 | 9.6 | 1 | ea | 12000 | 12000 | PGPC | NO | 2025 |  | 2: 12000
| Eastside Family Resource Center | HVAC | Heating | Replace building heating system gate valves |  |  |  |  | 2024 |  | N/A | 2 | 4 | 2 | 9.6 | 1 | ls | 10000 | 10000 | PGPC | NO | 2031 |  | 8: 10000
| Emma L Johnston Southside Family Resource Center | HVAC | Air Conditioning | Replace air conditioning system for 1st floor which is at end of life |  | AIR CONDITIONER |  |  | 2024 |  | N/A | 4 | 2 | 2 | 9.6 | 1 | ls | 10000 | 10000 | PGPC | NO | 2025 |  | 2: 10000
| County South Family Resource Center | Interior | Other | perform a feasibility study for construction of an enclosed stair landing to access the 2nd floor community room with interior connection to the front entry vestibule |  |  |  |  | 2024 |  | N/A | 4 | 2 | 2 | 9.6 | 1 | ea | 7500 | 7500 | PGPC | NO | 2025 |  | 2: 7500
| Eastside Family Resource Center | Site | Paving and Curbing | Repave and restripe west end parking lot; coordinate to occur after roof and site drainage work. Incorporate threshold and west egress point elevations to mitigate any potential basement flooding issues. |  |  |  |  | 2024 |  | N/A | 4 | 2 | 2 | 9.6 | 2000 | sf | 3 | 6000 | PGPC | NO | 2026 |  | 3: 6000
| Westside Family Resource Center | HVAC | Ventilating | Replace existing failed ductwork branches in basement |  |  |  |  | 2024 |  | N/A | 4 | 2 | 2 | 9.6 | 1 | ls | 5000 | 5000 | PGPC | NO | 2025 |  | 2: 5000
| Eastside Family Resource Center | Plumbing | Domestic HW Heating System | Replace DW heater |  | DOMESTIC HOT WATER HEATER GAS |  | 2007 | 17 | 20 | 3 | 4 | 2 | 2 | 9.6 | 1 | ea | 2500 | 2500 | PGPC | NO | 2024 |  | 1: 2500 |  | strategy for modifying existing bathroom exhaust will vary by existing conditions and fesibility. Likely to include general construction work.
| Transportation Department | HVAC | Heating | Extend boiler safety relief valve vent piping to outdoors as per Code. Valve is not piped currently. Failure could lead to significant loss of equipment in room. |  | BOILER, NATURAL GAS |  |  | 2024 |  | N/A | 2 | 4 | 2 | 9.6 | 1 | ls | 2000 | 2000 | PGPC | NO | 2024 |  | 1: 2000
| County South Family Resource Center | Envelope | Insulation | Investigate attic insulation and determine cause of ice dams | [6 empty] | N/A | 4 | 2 | 2 | 9.6 | 1 | ls | 1500 | 1500 | PGPC | NO | 2028 |  | 5: 1500
| Sumner Head Start & Big Brothers Big Sisters | HVAC | Energy | Remove roof ventilators over gymnasium. Heat vents are not used for summer anymore as originally intended and lead to increased building energy consumption in winter. |  |  |  |  | 2024 |  | N/A | 4 | 2 | 1 | 8.8 | 4 | ea | 2700 | 10800 | PGPC | NO | 2028 |  | 5: 10800
| DeFrancisco Eastwood Community Center | Envelope | Maintenance | Repair lower roof at first floor entry, repoint brick and repair entry door |  |  |  |  | 2024 |  | N/A | 4 | 2 | 1 | 8.8 | 1 | ea | 10000 | 10000 | PGPC | NO | 2025 |  | 2: 10000
| Merrick Head Start | Site | Flatwork / Sidewalks | Replace (17) sidewalk flags |  |  |  |  | 2024 |  | N/A | 4 | 2 | 1 | 8.8 | 17 | ea | 500 | 8500 | PGPC | NO | 2030 |  | 7: 8500
| DeFrancisco Eastwood Community Center | Site | Topology and Drainage | Adjust grade and extend existing window wells to mitigate surface runoff and flooding concerns |  |  |  |  | 2024 |  | N/A | 4 | 2 | 1 | 8.8 | 1 | ea | 7500 | 7500 | PGPC | NO | 2025 |  | 2: 7500
| Sumner Head Start & Big Brothers Big Sisters | HVAC | Capital Improvement | Improve air conditioning/supply airflow to rooms 104 & 107. Air balance duct system. |  | AIR CONDITIONER |  |  | 2024 |  | N/A | 4 | 2 | 1 | 8.8 | 1 | ea | 4800 | 4800 | PGPC | NO | 2030 |  | 7: 4800
| Merrick Head Start | HVAC | Ventilating | Replace kitchen wall exhaust fan |  | EXHAUST FAN |  |  | 2024 |  | N/A | 4 | 2 | 1 | 8.8 | 1 | ea | 1000 | 1000 | PGPC | NO | 2026 |  | 3: 1000
| LaFayette Head Start | HVAC | Other | Remove kitchen vent outlet backdraft damper to reduce airflow restriction from hood |  |  |  |  | 2024 |  | N/A | 4 | 2 | 1 | 8.8 | 1 | ea | 500 | 500 | PGPC | NO | 2030 |  | 7: 500
| Emma L Johnston Southside Family Resource Center | Security | Devices | Review whether sensitivity adjustment is feasible to reduce nuisance tripping of motion detectors |  |  |  |  | 2024 |  | N/A | 4 | 2 | 1 | 8.8 | 1 | ea | 0 | 0 | PGPC | NO | 2025 |  | 2: 0
| DeFrancisco Eastwood Community Center | HVAC | Air Conditioning | Provide split system A/C for hydaulic elevator machine room to maintain acceptable ambient temperature for elevator electronics. |  |  |  |  | 2024 |  | N/A | 2 | 3 | 4 | 8.4 | 1 | ls | 7000 | 7000 | PGPC | NO | 2025 |  | 2: 7000
| LaFayette Head Start | Plumbing | Domestic HW Heating System | Replace hot water heater at end of service life. | 101088 | DOMESTIC HOT WATER HEATER ELECTRIC | YES | 2021 | 3 | 12 | 9 | 2 | 3 | 4 | 8.4 | 1 | ls | 2500 | 2500 | PGPC | NO | 2031 |  | 8: 2500
| Merrick Head Start | Envelope | Windows | Replace remaining windows that have not been replaced from previous work |  |  |  |  | 2024 |  | N/A | 3 | 2 | 3 | 7.8 | 8 | ea | 10000 | 80000 | PGPC | NO | 2029 |  | 6: 80000
E.1.d.5 | LaFayette Head Start | HVAC | Air Conditioning | Replace R-22 A/C system for Classrooms | 101130 | CONDENSER FOR HVAC | YES | 2014 | 10 | 20 | 10 | 2 | 3 | 3 | 7.8 | 1 | ea | 20000 | 20000 | PGPC | NO | 2034 |  | 11: 20000
| Transportation Department | HVAC | Capital Improvement | No branch isolation valves for mains in boiler room or for temperature control valve servicing. Provide service isolation valves. |  | FLUID LOOP |  |  | 2024 |  | N/A | 2 | 3 | 3 | 7.8 | 1 | ls | 3000 | 3000 | PGPC | NO | 2024 |  | 1: 3000
| DeFrancisco Eastwood Community Center | Plumbing | Natural Gas System | Provide dirt/sediment legs on duct furnaces upstream of gas valves for protection. (Qty 2) |  |  | YES | 2003 | 21 | 25 | 4 | 2 | 3 | 3 | 7.8 | 2 | ls | 500 | 1000 | PGPC | NO | 2027 |  | 4: 1000
| Westside Family Resource Center | Miscellaneous | General | Engage in pest management services to follow up on potential rodent issue |  |  |  |  | 2024 |  | N/A | 3 | 2 | 3 | 7.8 | 1 | ls | 500 | 500 | PGPC | NO | 2025 |  | 2: 500
| Merrick Head Start | HVAC | Heating | Replace natural gas boiler | 101066 | BOILER, NATURAL GAS | YES | 2021 | 3 | 25 | 22 | 1 | 5 | 5 | 7.5 | 1 | ea | 30000 | 30000 | RSMeans | NO | Beyond | [12 empty] | 30000
| Sumner Head Start & Big Brothers Big Sisters | HVAC | Capital Improvement | Gym lacking summer ventilation capability. Provide new HVAC system for gym to replace old steam H&V unit. |  |  |  |  | 2024 |  | N/A | 3 | 2 | 2 | 7.2 | 1 | ea | 45000 | 45000 | PGPC | NO | 2029 |  | 6: 45000
| Sumner Head Start & Big Brothers Big Sisters | Plumbing | Domestic HW Heating System | Replace domestic hot water storage tank |  |  | NO | 2014 | 10 | 20 | 10 | 3 | 2 | 2 | 7.2 | 1 | ea | 10000 | 10000 | PGPC | NO | 2034 |  | 11: 10000
| Westside Family Resource Center | HVAC | Ventilating | Modify and upgrade bathroom exhaust ventilation |  | EXHAUST FAN |  |  | 2024 |  | N/A | 3 | 2 | 2 | 7.2 | 1 | ls | 5000 | 5000 | PGPC | NO | 2028 |  | 5: 5000
| DeFrancisco Eastwood Community Center | Interior | Ceiling | Repaint and ceilings mezzanine |  |  |  |  | 2024 |  | N/A | 3 | 2 | 2 | 7.2 | 1 | ea | 3500 | 3500 | PGPC | NO | 2027 |  | 4: 3500
| Transportation Department | HVAC | Capital Improvement | Install strainers to protect failing thermostatic radiator valves |  | FLUID LOOP |  |  | 2024 |  | N/A | 3 | 2 | 2 | 7.2 | 7 | ea | 500 | 3500 | PGPC | NO | 2024 |  | 1: 3500
| Westside Family Resource Center | HVAC | Air Conditioning | Correct heat pump condensate piping to connect to a pumped drain terminating outside the building |  |  |  |  | 2024 |  | N/A | 3 | 2 | 2 | 7.2 | 1 | ls | 2500 | 2500 | PGPC | NO | 2025 |  | 2: 2500
| Transportation Department | HVAC | Heating | Replace boiler flue in mech room and inspect stack. |  | BOILER, NATURAL GAS | NO | 1999 | 25 | 27 | 2 | 3 | 2 | 2 | 7.2 | 1 | ls | 1000 | 1000 | PGPC | NO | 2027 |  | 4: 1000
| County South Family Resource Center | Plumbing | Domestic HW Heating System | Water heaters should be blown down at the drain valve and inspected for corrosion of the storage tank |  | DOMESTIC HOT WATER HEATER GAS |  |  | 2024 |  | N/A | 3 | 2 | 2 | 7.2 | 1 | ea | 250 | 250 | PGPC | NO | 2024 |  | 1: 250
| Sumner Head Start & Big Brothers Big Sisters | HVAC | Capital Improvement | Boiler room combustion air intake louver too low at grade. Louver will be blocked by heavy snowfall. Provide intake pit infront of louver. |  |  |  |  | 2024 |  | N/A | 3 | 2 | 1 | 6.6 | 1 | ea | 15000 | 15000 | PGPC | NO | 2026 |  | 3: 15000
| Westside Family Resource Center | Electrical | Power | Update circuit breakers to GFCI and AFCI for facility protection |  |  |  |  | 2024 |  | N/A | 2 | 3 | 1 | 6.6 | 1 | ls | 10000 | 10000 | PGPC | NO | 2025 |  | 2: 10000
| Westside Family Resource Center | HVAC | Heating | Provide make up air for basement boiler room |  |  |  |  | 2024 |  | N/A | 3 | 2 | 1 | 6.6 | 1 | ls | 3000 | 3000 | PGPC | NO | 2025 |  | 2: 3000
| DeFrancisco Eastwood Community Center | HVAC | Heating | Provide makeup air to basement |  |  |  |  | 2024 |  | N/A | 3 | 2 | 1 | 6.6 | 1 | ls | 2500 | 2500 | PGPC | NO | 2030 |  | 7: 2500
| Eastside Family Resource Center | Electrical | Site Lighting | Replace existing floodlights for better illumination and safety |  |  |  |  | 2024 |  | N/A | 2 | 3 | 1 | 6.6 | 1 | ea | 2500 | 2500 | PGPC | NO | 2029 |  | 6: 2500
| DeFrancisco Eastwood Community Center | HVAC | Ventilating | Replace existing power roof fan for 2nd floor restrooms |  |  |  |  | 2024 |  | N/A | 2 | 3 | 1 | 6.6 | 1 | ls | 2000 | 2000 | PGPC | NO | 2029 |  | 6: 2000
| Westside Family Resource Center | Plumbing | Domestic Water Supply | Install RPZ backflow preventer for boiler heating system connection |  | BACKFLOW PREVENTER |  |  | 2024 |  | N/A | 3 | 2 | 1 | 6.6 | 1 | ls | 1500 | 1500 | PGPC | NO | 2027 |  | 4: 1500
| 717 Erie Boulevard West | Envelope | Maintenance | Reattach insulation on interior side of exterior wall, northwest corner/west side |  |  |  |  | 2024 |  | N/A | 3 | 2 | 1 | 6.6 | 1 | ls | 1000 | 1000 | PGPC | NO | 2024 |  | 1: 1000
| DeFrancisco Eastwood Community Center | HVAC | Heating | Investigate and inspect boiler flue stack integrity |  |  |  |  | 2024 |  | N/A | 2 | 3 | 1 | 6.6 | 1 | ls | 1000 | 1000 | PGPC | NO | 2025 |  | 2: 1000
| Emma L Johnston Southside Family Resource Center | Electrical | Site Lighting | Replace exterior floodlights |  |  |  |  | 2024 |  | N/A | 2 | 3 | 1 | 6.6 | 3 | ea | 200 | 600 | PGPC | NO | 2030 |  | 7: 600
| Merrick Head Start | Envelope | Maintenance | Correct potential hazardous condition in boiler room from water infiltration and algae growth. |  |  |  |  | 2024 |  | N/A | 3 | 2 | 1 | 6.6 | 1 | ea | 400 | 400 | PGPC | NO | 2025 |  | 2: 400
| Merrick Head Start | HVAC | Ventilating | Gymnasium lacking summer ventilation capability. Provide modern heating/cooling system with ventilation control. |  |  |  |  | 2024 |  | N/A | 5 | 1 | 3 | 6.5 | 1 | ea | 45000 | 45000 | PGPC | NO | 2030 |  | 7: 45000
| Merrick Head Start | HVAC | Air Conditioning | Replace rooftop A/C unit at end of life. Unit serves 2nd floor south classrooms | 101017 | AIR CONDITIONER | YES | 2022 | 2 | 15 | 13 | 1 | 4 | 5 | 6 | 1 | ea | 20000 | 20000 | PGPC | NO | Beyond | [12 empty] | 20000
| Merrick Head Start | HVAC | Air Conditioning | Replace rooftop A/C unit at end of life. Unit serves 2nd floor north classrooms |  | AIR CONDITIONER | YES | 2022 | 2 | 15 | 13 | 1 | 4 | 5 | 6 | 1 | ea | 20000 | 20000 | PGPC | NO | Beyond | [12 empty] | 20000
| Sumner Head Start & Big Brothers Big Sisters | Miscellaneous | ADA | Install one ADA lavatory in each Men's and Women's restrooms. |  | PLUMBING FIXTURE |  |  | 2024 |  | N/A | 5 | 1 | 2 | 6 | 4 | ea | 2500 | 10000 | PGPC | NO | 2025 |  | 2: 10000
| Sumner Head Start & Big Brothers Big Sisters | Interior | Maintenance | Repair damaged ceiling tiles over 2nd floor corridor. Inspect source of water infiltration |  |  |  |  | 2024 |  | N/A | 5 | 1 | 2 | 6 | 4 | ea | 50 | 200 | PGPC | NO | 2025 |  | 2: 200
| Sumner Head Start & Big Brothers Big Sisters | Envelope | Roofing | Replace roof drains, total of 12, and provide emergency overflows or scuppers |  | ROOF DRAIN |  | 1997 | 27 | 30 | 3 | 1 | 4 | 4 | 5.6 | 1 | ls | 25000 | 25000 | PGPC | NO | 2028 |  | 5: 25000
| Merrick Head Start | HVAC | Ventilating | Provide ducted exhaust to outdoors for classroom restrooms per Code. Existing non-compliant condition. |  |  |  |  | 2024 |  | N/A | 5 | 1 | 1 | 5.5 | 8 | ea | 5000 | 40000 | PGPC | NO | 2027 |  | 4: 40000
| Westside Family Resource Center | HVAC | Ventilating | Consider mechanical ventilation system to provide Code required ventilation rates |  |  |  |  | 2024 |  | N/A | 5 | 1 | 1 | 5.5 | 1 | ls | 25000 | 25000 | PGPC | NO | 2025 |  | 2: 25000
| Transportation Department | HVAC | Ventilating | Provide energy recovery ventilation unit for dedicated ventilation for offices and exhaust for restrooms. Remove restroom exhaust fans and cap wall openings. |  |  |  | 1960 | 64 | 50 | -14 | 5 | 1 | 1 | 5.5 | 1 | ls | 22000 | 22000 | PGPC | NO | 2024 |  | 1: 22000
| Merrick Head Start | HVAC | Ventilating | Install gas line for rooftop units for heating. Gas currently not hooked up. |  |  |  |  | 2024 |  | N/A | 5 | 1 | 1 | 5.5 | 2 | ea | 10000 | 20000 | PGPC | NO | 2031 |  | 8: 20000
| 717 Erie Boulevard West | HVAC | Controls | Investigate and connect VAV controls |  | NET CONTROLLER |  |  | 2024 |  | N/A | 5 | 1 | 1 | 5.5 | 1 | ls | 15000 | 15000 | PGPC | NO | 2027 |  | 4: 15000
| Emma L Johnston Southside Family Resource Center | Envelope | Windows | Repair and replace broken windows and screens |  |  |  |  | 2024 |  | N/A | 5 | 1 | 1 | 5.5 | 1 | ea | 15000 | 15000 | PGPC | NO | 2030 |  | 7: 15000
| Transportation Department | Envelope | Façade | Replace failing vinyl siding west exposure of building |  |  |  |  | 2024 |  | N/A | 5 | 1 | 1 | 5.5 | 1 | ls | 15000 | 15000 | PGPC | NO | 2028 |  | 5: 15000
| Sumner Head Start & Big Brothers Big Sisters | HVAC | Energy | Insulate steam piping and condensate piping in mechanical room where missing. |  | FLUID LOOP |  |  | 2024 |  | N/A | 5 | 1 | 1 | 5.5 | 1 | ea | 12000 | 12000 | PGPC | NO | 2030 |  | 7: 12000
| LaFayette Head Start | Plumbing | Domestic HW Heating System | Insulate HW piping and provide recirc system for restrooms as required per Code |  |  |  |  | 2024 |  | N/A | 5 | 1 | 1 | 5.5 | 1 | ls | 7000 | 7000 | PGPC | NO | 2024 |  | 1: 7000
| 717 Erie Boulevard West | Envelope | Insulation | Window repairs to cracked and compromised seals |  |  |  |  | 2024 |  | N/A | 5 | 1 | 1 | 5.5 | 1 | ea | 5000 | 5000 | PGPC | NO | 2029 |  | 6: 5000
| DeFrancisco Eastwood Community Center | HVAC | Ventilating | Site water entered elevator machine room during heavy rain. Remove exhaust duct for machine room. Provide ventilation for machine room. |  |  |  |  | 2024 |  | N/A | 5 | 1 | 1 | 5.5 | 1 | ea | 5000 | 5000 | PGPC | NO | 2027 |  | 4: 5000
| Sumner Head Start & Big Brothers Big Sisters | Site | Paving and Curbing | West parking lot in fair condition. Just needs to be re-striped for proper vehicle spacing. |  |  |  |  | 2024 |  | N/A | 5 | 1 | 1 | 5.5 | 1 | ea | 5000 | 5000 | PGPC | NO | 2028 |  | 5: 5000
| County South Family Resource Center | Envelope | Maintenance | Repair missing siding to limit water infiltration into north exterior wall |  |  |  |  | 2024 |  | N/A | 5 | 1 | 1 | 5.5 | 1 | ea | 3000 | 3000 | PGPC | NO | 2026 |  | 3: 3000
| Eastside Family Resource Center | Site | Flatwork / Sidewalks | Replace failed sidewalk flags |  |  |  |  | 2024 |  | N/A | 5 | 1 | 1 | 5.5 | 6 | ea | 500 | 3000 | PGPC | NO | 2030 |  | 7: 3000
| Eastside Family Resource Center | Plumbing | Energy | Insulate domestic HW piping |  |  |  |  | 2024 |  | N/A | 5 | 1 | 1 | 5.5 | 1 | ls | 2500 | 2500 | PGPC | NO | 2031 |  | 8: 2500
| Merrick Head Start | Electrical | Power | Repair lightning protection system |  |  |  |  | 2024 |  | N/A | 5 | 1 | 1 | 5.5 | 1 | ea | 2500 | 2500 | PGPC | NO | 2032 |  | 9: 2500
| Westside Family Resource Center | HVAC | Energy | Install pipe insulation on hydronic heating HW piping per NYS Energy Code |  | FLUID LOOP |  |  | 2024 |  | N/A | 5 | 1 | 1 | 5.5 | 1 | ls | 2500 | 2500 | PGPC | NO | 2025 |  | 2: 2500
| Emma L Johnston Southside Family Resource Center | Electrical | Site Lighting | Repair exterior signage which is currently non-functioning |  |  |  |  | 2024 |  | N/A | 5 | 1 | 1 | 5.5 | 1 | ea | 2000 | 2000 | PGPC | NO | 2025 |  | 2: 2000
| Merrick Head Start | Plumbing | Backflow Prevention | Provide backflow prevention for mop sink supplies. Install check valves. |  | BACKFLOW PREVENTER |  |  | 2024 |  | N/A | 5 | 1 | 1 | 5.5 | 1 | ea | 2000 | 2000 | PGPC | NO | 2027 |  | 4: 2000
| Merrick Head Start | HVAC | Heating | Repair or replace leaking steam gate valve at gymnasium H&V air handling unit located at south stage mech room. |  |  |  |  | 2024 |  | N/A | 5 | 1 | 1 | 5.5 | 1 | ea | 1000 | 1000 | PGPC | NO | 2025 |  | 2: 1000
| Merrick Head Start | HVAC | Capital Improvement | Upgrade building temperature controls to avoid overheating in winter and excessive energy consumption. |  | NET CONTROLLER |  |  | 2024 |  | N/A | 2 | 2 | 3 | 5.2 | 1 | ea | 100000 | 100000 | PGPC | NO | 2031 |  | 8: 100000
| DeFrancisco Eastwood Community Center | HVAC | Ventilating | Outside air dampers for basement air handling units not functioning properly. Investigate issue and correct problem. Building not being ventilated. | 101080/ 101022 | AIR CONDITIONER | YES | 2003 | 21 | 20 | -1 | 4 | 1 | 3 | 5.2 | 2 | ls | 5000 | 10000 | PGPC | NO | 2024 |  | 1: 10000
| Eastside Family Resource Center | Miscellaneous | Capital Improvement | Install ceiling and exhaust fan to reduce overheating of space at existing basement refrigeration equipment |  |  |  |  | 2024 |  | N/A | 2 | 2 | 3 | 5.2 | 1 | ea | 10000 | 10000 | PGPC | NO | 2032 |  | 9: 10000
| Merrick Head Start | Plumbing | Domestic HW Heating System | DHW storage tank replacement |  |  | NO | 2014 | 10 | 25 | 15 | 1 | 4 | 3 | 5.2 | 1 | ea | 10000 | 10000 | PGPC | NO | Beyond | [12 empty] | 10000
| Merrick Head Start | HVAC | Air Conditioning | Gymnasium A/C unit condenser operating in winter with indoor unit off. Provide proper owner training for switching system off for winter. |  | CONDENSER FOR HVAC | NO | 2022 | 2 | 20 | 18 | 2 | 2 | 3 | 5.2 | 1 | ea | 500 | 500 | PGPC | NO | 2025 |  | 2: 500
| Sumner Head Start & Big Brothers Big Sisters | HVAC | Capital Improvement | Provide better air circulation for gym. Install HVLS fans to provide cooling effect in summer. |  |  |  |  | 2024 |  | N/A | 2 | 2 | 2 | 4.8 | 2 | ea | 14000 | 28000 | PGPC | NO | 2028 |  | 5: 28000
| Eastside Family Resource Center | Electrical | Interior Lighting | Consider upgrades to lighting for better aesthetics and control |  |  |  |  | 2024 |  | N/A | 2 | 2 | 2 | 4.8 | 1 | ea | 25000 | 25000 | PGPC | NO | 2031 |  | 8: 25000
| Eastside Family Resource Center | Plumbing | Interior Sanitary Drainage | Code may require separation of sanitary from storm system within the building |  |  |  |  | 2024 |  | N/A | 2 | 2 | 2 | 4.8 | 1 | ls | 20000 | 20000 | PGPC | NO | Beyond | [12 empty] | 20000
| LaFayette Head Start | Electrical | Power | Replace obsolete power panels with more modern equipment |  | ELECTRIC PANEL |  |  | 2024 |  | N/A | 2 | 2 | 2 | 4.8 | 1 | ea | 15000 | 15000 | PGPC | NO | 2030 |  | 7: 15000
| Merrick Head Start | Miscellaneous | ADA | Provide ADA bi-level drinking fountain |  | PLUMBING FIXTURE |  |  | 2024 |  | N/A | 2 | 2 | 2 | 4.8 | 2 | ea | 6200 | 12400 | PGPC | NO | 2031 |  | 8: 12400
| Sumner Head Start & Big Brothers Big Sisters | Miscellaneous | ADA | Provide ADA bi-level drinking fountain |  | PLUMBING FIXTURE |  |  | 2024 |  | N/A | 2 | 2 | 2 | 4.8 | 2 | ea | 6200 | 12400 | PGPC | NO | 2029 |  | 6: 12400
| Emma L Johnston Southside Family Resource Center | HVAC | Ventilating | Perform bathroom ventilation improvements for restrooms |  |  |  |  | 2024 |  | N/A | 4 | 1 | 2 | 4.8 | 1 | ea | 7500 | 7500 | PGPC | NO | 2027 |  | 4: 7500
| DeFrancisco Eastwood Community Center | Site | Paving and Curbing | Re-stripe parking lot, including the designation of an accessible parking space |  |  |  |  | 2024 |  | N/A | 4 | 1 | 2 | 4.8 | 1 | ea | 7000 | 7000 | PGPC | NO | 2028 |  | 5: 7000
| Emma L Johnston Southside Family Resource Center | HVAC | Other | Install UL Listed range hood above 1st floor kitchen appliance to meet Code |  |  |  |  | 2024 |  | N/A | 2 | 2 | 2 | 4.8 | 1 | ea | 5000 | 5000 | PGPC | NO | 2029 |  | 6: 5000
| Sumner Head Start & Big Brothers Big Sisters | Miscellaneous | General | Test for radon |  |  |  |  | 2024 |  | N/A | 2 | 2 | 2 | 4.8 | 1 | ls | 5000 | 5000 | PGPC | NO | 2025 |  | 2: 5000
| Westside Family Resource Center | HVAC | Air Conditioning | Replace heat pump in 1st floor reception area | 101027 | HEAT PUMP |  |  | 2024 |  | N/A | 2 | 2 | 2 | 4.8 | 1 | ls | 5000 | 5000 | PGPC | NO | 2034 |  | 11: 5000
| Westside Family Resource Center | HVAC | Air Conditioning | Replace heat pump in 2nd floor kitchen area | 101025 | HEAT PUMP |  |  | 2024 |  | N/A | 2 | 2 | 2 | 4.8 | 1 | ls | 5000 | 5000 | PGPC | NO | 2034 |  | 11: 5000
| Eastside Family Resource Center | HVAC | Heating | Investigate condition of hydronic heating system for corrosion |  |  |  |  | 2024 |  | N/A | 2 | 2 | 2 | 4.8 | 1 | ls | 2500 | 2500 | PGPC | NO | 2031 |  | 8: 2500
| County South Family Resource Center | Miscellaneous | General | Test for radon |  |  |  |  | 2024 |  | N/A | 2 | 2 | 2 | 4.8 | 1 | ls | 1500 | 1500 | PGPC | NO | 2025 |  | 2: 1500
| Eastside Family Resource Center | Miscellaneous | General | Test for radon |  |  |  |  | 2024 |  | N/A | 2 | 2 | 2 | 4.8 | 1 | ls | 1500 | 1500 | PGPC | NO | 2025 |  | 2: 1500
| Eastside Family Resource Center | Envelope | Maintenance | Replace basement rear egress door for security and draft / infiltration purposes |  |  |  |  | 2024 |  | N/A | 4 | 1 | 2 | 4.8 | 1 | ea | 1500 | 1500 | PGPC | NO | 2030 |  | 7: 1500
| Emma L Johnston Southside Family Resource Center | Miscellaneous | General | Test for radon |  |  |  |  | 2024 |  | N/A | 2 | 2 | 2 | 4.8 | 1 | ls | 1500 | 1500 | PGPC | NO | 2025 |  | 2: 1500
| LaFayette Head Start | HVAC | Capital Improvement | Install dedicated HVAC ventilation system to provide minimum mechanical ventilation rates |  |  |  |  | 2024 |  | N/A | 2 | 2 | 2 | 4.8 | 1 | ls | 1200 | 1200 | PGPC | NO | 2030 |  | 7: 1200
| DeFrancisco Eastwood Community Center | Miscellaneous | General | Test for radon |  |  |  |  | 2024 |  | N/A | 2 | 2 | 2 | 4.8 | 1 | ls | 1000 | 1000 | PGPC | NO | 2025 |  | 2: 1000
| Eastside Family Resource Center | Plumbing | Fixtures | Replace men's first floor restroom fixture with ADA type |  | PLUMBING FIXTURE |  |  | 2024 |  | N/A | 2 | 2 | 2 | 4.8 | 1 | ea | 1000 | 1000 | PGPC | NO | 2025 |  | 2: 1000
| Eastside Family Resource Center | Plumbing | Fixtures | Replace women's first floor restroom fixture with ADA type |  | PLUMBING FIXTURE |  |  | 2024 |  | N/A | 2 | 2 | 2 | 4.8 | 1 | ea | 1000 | 1000 | PGPC | NO | 2025 |  | 2: 1000
| Merrick Head Start | Plumbing | Backflow Prevention | Provide spring check valves on service sink supply lines to protect building domestic water system from backflow |  |  |  |  | 2024 |  | N/A | 2 | 2 | 2 | 4.8 | 1 | ls | 1000 | 1000 | PGPC | NO | 2029 |  | 6: 1000
| Westside Family Resource Center | Miscellaneous | General | Test for radon |  |  |  |  | 2024 |  | N/A | 2 | 2 | 2 | 4.8 | 1 | ls | 1000 | 1000 | PGPC | NO | 2025 |  | 2: 1000
| 717 Erie Boulevard West | Miscellaneous | General | Test for radon |  |  |  |  | 2024 |  | N/A | 2 | 2 | 2 | 4.8 | 1 | ls | 750 | 750 | PGPC | NO | 2025 |  | 2: 750
| DeFrancisco Eastwood Community Center | Plumbing | Interior Sanitary Drainage | Replace missing floor grates to prevent objects from becoming trapped in piping system |  | FLOOR DRAIN |  |  | 2024 |  | N/A | 2 | 2 | 2 | 4.8 | 1 | ls | 500 | 500 | PGPC | NO | 2025 |  | 2: 500
| DeFrancisco Eastwood Community Center | HVAC | Controls | Consider controls upgrade simultaneous to AHU - duct furnace replacement |  |  |  |  | 2024 |  | N/A | 2 | 2 | 1 | 4.4 | 1 | ls | 40000 | 40000 | PGPC | NO | Beyond | [12 empty] | 40000
| Sumner Head Start & Big Brothers Big Sisters | Plumbing | Energy | Insulate plumbing domestic hot water piping where not insulated in basement and crawlspace |  | FLUID LOOP |  |  | 2024 |  | N/A | 4 | 1 | 1 | 4.4 | 1 | ea | 25000 | 25000 | PGPC | NO | 2030 |  | 7: 25000
| LaFayette Head Start | Site | Flatwork / Sidewalks | Sidewalk repairs |  |  |  |  | 2024 |  | N/A | 4 | 1 | 1 | 4.4 | 1 | ls | 20000 | 20000 | PGPC | NO | 2029 |  | 6: 20000
| Merrick Head Start | Electrical | Capital Improvement | Replace older power panels with newer equipment. |  | ELECTRIC PANEL |  |  | 2024 |  | N/A | 2 | 2 | 1 | 4.4 | 1 | ls | 20000 | 20000 | PGPC | NO | 2031 |  | 8: 20000
| Eastside Family Resource Center | HVAC | Heating | Install insulation on hydronic system piping |  |  |  |  | 2024 |  | N/A | 4 | 1 | 1 | 4.4 | 1 | ls | 10000 | 10000 | PGPC | NO | 2027 |  | 4: 10000
| Emma L Johnston Southside Family Resource Center | Electrical | Interior Lighting | Replace interior lighting fixtures |  |  |  |  | 2024 |  | N/A | 2 | 2 | 1 | 4.4 | 1 | ls | 10000 | 10000 | PGPC | NO | 2030 |  | 7: 10000
| Merrick Head Start | HVAC | Heating | Install louver and insulated low-leakage motorized damper interlocked with the operation of the boiler burner. Add'l work required to relocate existing plumbing piping |  |  |  |  | 2024 |  | N/A | 2 | 2 | 1 | 4.4 | 1 | ea | 10000 | 10000 | PGPC | NO | 2028 |  | 5: 10000
| Merrick Head Start | Site | Paving and Curbing | Restripe parking lines |  |  |  |  | 2024 |  |  | 4 | 1 | 1 | 4.4 | 1 | ea | 7500 | 7500 | PGPC | NO | 2027 |  | 4: 7500
| Westside Family Resource Center | Site | Paving and Curbing | Restripe parking lines |  |  |  |  | 2024 |  | N/A | 4 | 1 | 1 | 4.4 | 1 | ea | 7500 | 7500 | PGPC | NO | 2027 |  | 4: 7500
| Merrick Head Start | HVAC | Energy | Remove roof ventilators over gymnasium. Heat vents are not used for summer anymore as originally intended and lead to increased building energy consumption in winter. |  |  |  |  | 2024 |  | N/A | 4 | 1 | 1 | 4.4 | 2 | ea | 2700 | 5400 | PGPC | NO | 2030 |  | 7: 5400
| DeFrancisco Eastwood Community Center | HVAC | Air Conditioning | Replace conduit and wiring on unit, remove soils from piping, provide protective enclosure, insulation and protective covers |  |  |  |  | 2024 |  | N/A | 2 | 2 | 1 | 4.4 | 1 | ls | 5000 | 5000 | PGPC | NO | 2027 |  | 4: 5000
3.f | Merrick Head Start | HVAC | Ventilating | Replace grease exhaust fan for kitchen hood |  | EXHAUST FAN |  |  | 2024 |  | N/A | 2 | 2 | 1 | 4.4 | 1 | ea | 5000 | 5000 | PGPC | NO | 2029 |  | 6: 5000
| Merrick Head Start | Envelope |  | Brick repair SE corner of building |  |  |  |  | 2024 |  | N/A | 2 | 2 | 1 | 4.4 | 1 | ea | 5000 | 5000 | PGPC | NO | 2027 |  | 4: 5000
| Merrick Head Start | HVAC | Energy | Remove abandoned gym H&V unit at south stage and cap duct connections to exterior. Openings to outdoors lead to increased building energy consumption in winter. |  | HEATING AND VENTILATION UNITS |  |  | 2024 |  | N/A | 4 | 1 | 1 | 4.4 | 1 | ea | 4000 | 4000 | PGPC | NO | 2029 |  | 6: 4000
| Transportation Department | Site | Paving and Curbing | Restripe parking lines on the floor of the building |  |  |  |  | 2024 |  | N/A | 4 | 1 | 1 | 4.4 | 1 | ea | 3000 | 3000 | PGPC | NO | 2030 |  | 7: 3000
| Emma L Johnston Southside Family Resource Center | HVAC | Ventilating | Perform ventilation ductwork modifications and sealing |  |  |  |  | 2024 |  | N/A | 2 | 2 | 1 | 4.4 | 1 | ls | 2500 | 2500 | PGPC | NO | 2028 |  | 5: 2500
| LaFayette Head Start | Plumbing | Domestic Water Supply | Replace water conditioner (softener) at end of service life | 101085 |  | YES | 2016 | 8 | 15 | 7 | 2 | 2 | 1 | 4.4 | 1 | ea | 2500 | 2500 | PGPC | NO | 2031 |  | 8: 2500
| DeFrancisco Eastwood Community Center | HVAC | Capital Improvement | Consider battery or backup power supply on control system to communicate alarm conditions to service team in the event of a power outage |  |  |  |  | 2024 |  | N/A | 2 | 2 | 1 | 4.4 | 1 | ls | 2000 | 2000 | PGPC | NO | 2028 |  | 5: 2000
| Sumner Head Start & Big Brothers Big Sisters | Plumbing | Domestic Water Supply | Inspect and repalce shock arrestors on Domestic HW and CW |  | FLUID LOOP |  |  | 2024 |  | N/A | 2 | 2 | 1 | 4.4 | 1 | ls | 2000 | 2000 | PGPC | NO | 2029 |  | 6: 2000
| Westside Family Resource Center | Interior | Maintenance | Investigate and repair potential leak in 1st floor office from AC evaporator unit condensate |  |  |  |  | 2024 |  | N/A | 2 | 2 | 1 | 4.4 | 1 | ls | 2000 | 2000 | PGPC | NO | 2025 |  | 2: 2000
| County South Family Resource Center | HVAC | Ventilating | Recommend extending ductwork for exhaust fan to an outdoor discharge terminal per Code |  | EXHAUST FAN |  |  | 2024 |  | N/A | 4 | 1 | 1 | 4.4 | 1 | ea | 1000 | 1000 | PGPC | NO | 2025 |  | 2: 1000
| DeFrancisco Eastwood Community Center | Plumbing | Energy | Provide missing insulation at basement water heater |  |  |  |  | 2024 |  | N/A | 2 | 2 | 1 | 4.4 | 1 | ls | 1000 | 1000 | PGPC | NO | 2027 |  | 4: 1000
| Sumner Head Start & Big Brothers Big Sisters | Plumbing | Capital Improvement | Extend RTU condensate drain lines to roof drain sumps to avoid surface standing water |  | AIR CONDITIONER |  |  | 2024 |  | N/A | 2 | 2 | 1 | 4.4 | 1 | ea | 800 | 800 | PGPC | NO | 2026 |  | 3: 800
| 717 Erie Boulevard West | Plumbing | Domestic Water Supply | Test for lead content levels in water supply. |  |  |  |  | 2024 |  | N/A | 1 | 4 | 1 | 4.4 | 1 | ls | 500 | 500 | PGPC | NO | 2025 |  | 2: 500
| County South Family Resource Center | Plumbing | Domestic Water Supply | Test for lead content levels in water supply. |  |  |  |  | 2024 |  | N/A | 1 | 4 | 1 | 4.4 | 1 | ls | 500 | 500 | PGPC | NO | 2025 |  | 2: 500
| DeFrancisco Eastwood Community Center | Plumbing | Domestic Water Supply | Test for lead content levels in water supply. |  |  |  |  | 2024 |  | N/A | 1 | 4 | 1 | 4.4 | 1 | ls | 500 | 500 | PGPC | NO | 2025 |  | 2: 500
| Eastside Family Resource Center | Plumbing | Domestic Water Supply | Test for lead content levels in water supply. |  |  |  |  | 2024 |  | N/A | 1 | 4 | 1 | 4.4 | 1 | ls | 500 | 500 | PGPC | NO | 2025 |  | 2: 500
| Emma L Johnston Southside Family Resource Center | Plumbing | Domestic Water Supply | Test for lead content levels in water supply. |  |  |  |  | 2024 |  | N/A | 1 | 4 | 1 | 4.4 | 1 | ls | 500 | 500 | PGPC | NO | 2025 |  | 2: 500
| LaFayette Head Start | Plumbing | Domestic Water Supply | Test for lead content levels in water supply. |  |  |  |  | 2024 |  | N/A | 1 | 4 | 1 | 4.4 | 1 | ls | 500 | 500 | PGPC | NO | 2025 |  | 2: 500
| Merrick Head Start | Plumbing | Domestic Water Supply | Test for lead content levels in water supply. |  |  |  |  | 2024 |  | N/A | 1 | 4 | 1 | 4.4 | 1 | ls | 500 | 500 | PGPC | NO | 2025 |  | 2: 500
| Sumner Head Start & Big Brothers Big Sisters | Plumbing | Domestic Water Supply | Test for lead content levels in water supply. |  |  |  |  | 2024 |  | N/A | 1 | 4 | 1 | 4.4 | 1 | ls | 500 | 500 | PGPC | NO | 2025 |  | 2: 500
| Transportation Department | Miscellaneous | General | Test for radon |  |  |  |  | 2024 |  | N/A | 2 | 2 | 1 | 4.4 | 1 | ls | 500 | 500 | PGPC | NO | 2025 |  | 2: 500
| Transportation Department | Plumbing | Domestic Water Supply | Test for lead content levels in water supply. |  |  |  |  | 2024 |  | N/A | 1 | 4 | 1 | 4.4 | 1 | ls | 500 | 500 | PGPC | NO | 2025 |  | 2: 500
| Westside Family Resource Center | Plumbing | Domestic Water Supply | Test for lead content levels in water supply. |  |  |  |  | 2024 |  | N/A | 1 | 4 | 1 | 4.4 | 1 | ls | 500 | 500 | PGPC | NO | 2025 |  | 2: 500
| LaFayette Head Start | Electrical | Site Lighting | Replace existing parking lot luminaire |  |  |  |  | 2024 |  | N/A | 4 | 1 | 1 | 4.4 | 1 | ea | 350 | 350 | PGPC | NO | 2026 |  | 3: 350
| LaFayette Head Start | HVAC | Other | Provide washable grease filters for kitchen range hood |  | FILTER |  |  | 2024 |  | N/A | 2 | 2 | 1 | 4.4 | 1 | ea | 250 | 250 | PGPC | NO | 2027 |  | 4: 250
| 717 Erie Boulevard West | Plumbing | Domestic HW Heating System | Replace electric DWH heater for main restrooms, 4.5kW. | 101018 | DOMESTIC HOT WATER HEATER ELECTRIC | YES | 2017 | 7 | 12 | 5 | 1 | 3 | 4 | 4.2 | 1 | ls | 2000 | 2000 | PGPC | NO | 2029 |  | 6: 2000
| Transportation Department | Electrical | Site Lighting | Provide replacement LED light over west entrance. |  |  | NO | 1995 | 29 | 30 | 1 | 3 | 1 | 3 | 3.9 | 1 | ls | 500 | 500 | PGPC | NO | 2025 |  | 2: 500
| Sumner Head Start & Big Brothers Big Sisters | HVAC | Air Conditioning | Reattach/secure access panel on rooftop unit RTU-3 |  | AIR CONDITIONER |  |  | 2024 |  | N/A | 1 | 3 | 3 | 3.9 | 1 | ea | 50 | 50 | PGPC | NO | 2025 |  | 2: 50
| Merrick Head Start | HVAC | Other | Study exhaust discharge from classroom private restrooms and determine proper ventilation requirements |  |  |  |  | 2024 |  | N/A | 3 | 1 | 2 | 3.6 | 1 | ea | 6000 | 6000 | PGPC | NO | 2026 |  | 3: 6000
| Eastside Family Resource Center | Plumbing | Capital Improvement | Provide Code required custodial storage area with service sink |  |  |  |  | 2024 |  | N/A | 3 | 1 | 2 | 3.6 | 1 | ls | 5000 | 5000 | PGPC | NO | 2028 |  | 5: 5000
| Transportation Department | HVAC | Ventilating | Remove old gravity vents and replace with new aluminum gravity vents with shutdown dampers. |  |  |  | 1960 | 64 | 50 | -14 | 3 | 1 | 1 | 3.3 | 2 | ea | 4000 | 8000 | PGPC | NO | 2027 |  | 4: 8000
| Sumner Head Start & Big Brothers Big Sisters | Miscellaneous | Maintenance | Inspect condition of boiler flue stack and chimney |  |  |  |  | 2024 |  | N/A | 3 | 1 | 1 | 3.3 | 1 | ea | 7000 | 7000 | PGPC | NO | 2027 |  | 4: 7000
| LaFayette Head Start | HVAC | Ventilating | Provide kitchen exhaust makeup air. |  |  |  |  | 2024 |  | N/A | 3 | 1 | 1 | 3.3 | 1 | ls | 5000 | 5000 | PGPC | NO | 2028 |  | 5: 5000
| Merrick Head Start | HVAC | Ventilating | Replace gymnasium grille covers to provide better heating |  |  |  |  | 2024 |  | N/A | 3 | 1 | 1 | 3.3 | 1 | ea | 5000 | 5000 | PGPC | NO | 2026 |  | 3: 5000
| Transportation Department | Envelope | Insulation | Rettach and replace blanket insulation on undersie of roof over the boiler and fuel/gas storage room |  | BOILER, NATURAL GAS |  |  | 2024 |  | N/A | 3 | 1 | 1 | 3.3 | 1 | ls | 5000 | 5000 | PGPC | NO | 2029 |  | 6: 5000
| Transportation Department | Plumbing | Domestic HW Heating System | Provide RPX backflow (Code required) on 3/4" connection to boiler system |  | BACKFLOW PREVENTER |  |  | 2024 |  | N/A | 3 | 1 | 1 | 3.3 | 1 | ls | 2500 | 2500 | PGPC | NO | 2026 |  | 3: 2500
| Transportation Department | Plumbing | Domestic Water Supply | Install RPZ backflor on 1-1/2" service downstream of meter |  | BACKFLOW PREVENTER |  |  | 2024 |  | N/A | 3 | 1 | 1 | 3.3 | 1 | ls | 2500 | 2500 | PGPC | NO | 2026 |  | 3: 2500
| LaFayette Head Start | Interior | Other | Remove / modify shelving to accommodate wheelchair turning radius |  |  |  |  | 2024 |  | N/A | 3 | 1 | 1 | 3.3 | 1 | ea | 1500 | 1500 | PGPC | NO | 2028 |  | 5: 1500
| LaFayette Head Start | Plumbing | Interior Sanitary Drainage | Plug floor drain or install trap seal in storage room of office at center/north end of bldg. |  | FLOOR DRAIN |  |  | 2024 |  | N/A | 3 | 1 | 1 | 3.3 | 1 | ea | 500 | 500 | PGPC | NO | 2025 |  | 2: 500
| LaFayette Head Start | Miscellaneous | General | Investigate Attic space and insulation |  |  |  |  | 2024 |  | N/A | 3 | 1 | 1 | 3.3 | 1 | ea | 500 | 500 | PGPC | NO | 2029 |  | 6: 500
| Transportation Department | Interior | Flooring | Replace VCT flooring |  |  |  |  | 2024 |  | N/A | 3 | 1 | 1 | 3.3 | 1 | ls | 500 | 500 | PGPC | NO | 2028 |  | 5: 500
| DeFrancisco Eastwood Community Center | HVAC | Capital Improvement | No local temperature control for kitchen which gets hot and is different thermal zone from AHU which serves area. Provide ductless split a/c system. |  |  |  |  | 2024 |  | N/A | 1 | 2 | 3 | 2.6 | 1 | ls | 15000 | 15000 | PGPC | NO | 2027 |  | 4: 15000
| DeFrancisco Eastwood Community Center | HVAC | Ventilating | Provide duct modifications to improve airflow and alleviate tenant temperature complaints in 2nd fl NE office 210. |  |  |  |  | 2024 |  | N/A | 1 | 2 | 3 | 2.6 | 1 | ls | 5000 | 5000 | PGPC | NO | 2025 |  | 2: 5000
| LaFayette Head Start | HVAC | Air Conditioning | Implement preventative maintenance schedule for cleaning outdoor condensing unit coil fins |  | CONDENSER FOR HVAC |  |  | 2024 |  | N/A | 2 | 1 | 2 | 2.4 | 1 | ls | 500 | 500 | PGPC | NO | 2030 |  | 7: 500
| LaFayette Head Start | HVAC | Air Conditioning | Raise and adjust grade around outdoor classroom condenser to extend equipment life |  |  |  |  | 2024 |  | N/A | 2 | 1 | 2 | 2.4 | 1 | ls | 500 | 500 | PGPC | NO | 2030 |  | 7: 500
| Merrick Head Start | Plumbing | Capital Improvement | Re-install DHW recirc pump in serviceable location |  | DOMESTIC HOT WATER PUMP |  |  | 2024 |  | N/A | 1 | 2 | 1 | 2.2 | 1 | ea | 2500 | 2500 | PGPC | NO | 2030 |  | 7: 2500
| Emma L Johnston Southside Family Resource Center | Site | Utilities | Reduce Gas meters from (3) to (1) to reduce additional billing |  |  |  |  | 2024 |  | N/A | 2 | 1 | 1 | 2.2 | 1 | ea | 1500 | 1500 | PGPC | NO | 2030 |  | 7: 1500
| 717 Erie Boulevard West | Plumbing | Backflow Prevention | Provide check valves on mop sink supplies as per plumbing code |  |  |  |  | 2024 |  | N/A | 1 | 2 | 1 | 2.2 | 1 | ls | 1000 | 1000 | PGPC | NO | 2024 |  | 1: 1000
| Merrick Head Start | HVAC | Air Conditioning | Remove old window A/C units. |  | AIR CONDITIONER |  |  | 2024 |  | N/A | 2 | 1 | 1 | 2.2 | 1 | ls | 500 | 500 | PGPC | NO | 2030 |  | 7: 500
| Transportation Department | Interior | Ceiling | Remove partial ACT ceiling in NW corner of garage |  |  |  |  | 2024 |  | N/A | 2 | 1 | 1 | 2.2 | 1 | ls | 500 | 500 | PGPC | NO | 2028 |  | 5: 500
| Eastside Family Resource Center | HVAC | Heating | Install programmable thermostat to preheat space before community events |  |  |  |  | 2024 |  | N/A | 1 | 1 | 5 | 1.5 | 1 | ea | 750 | 750 | PGPC | NO | 2025 |  | 2: 750
| Merrick Head Start | Plumbing | Capital Improvement | Provide redundant backflow preventer |  | BACKFLOW PREVENTER |  |  | 2024 |  | N/A | 1 | 1 | 4 | 1.4 | 1 | ea | 5000 | 5000 | PGPC | NO | 2032 |  | 9: 5000
| Transportation Department | HVAC | Heating | Insulate steam piping up to 6ft above floor for personell protection from hot surfaces per OSHA requirements |  | FLUID LOOP |  |  | 2024 |  | N/A | 1 | 1 | 4 | 1.4 | 1 | ls | 3000 | 3000 | PGPC | NO | 2024 |  | 1: 3000
| DeFrancisco Eastwood Community Center | Plumbing | Domestic HW Heating System | Provide domestic hot water recirculation system for restrooms per Code. |  | DOMESTIC HOT WATER HEATER GAS |  |  | 2024 |  | N/A | 1 | 1 | 3 | 1.3 | 1 | ls | 12000 | 12000 | PGPC | NO | 2027 |  | 4: 12000
| Merrick Head Start | Plumbing | Interior Sanitary Drainage | Re-route A/C cond line to storm, not grease manhole |  |  |  |  | 2024 |  | N/A | 1 | 1 | 3 | 1.3 | 1 | ea | 3000 | 3000 | PGPC | NO | 2031 |  | 8: 3000
| LaFayette Head Start | Miscellaneous | ADA | Provide vertical grab bars for ADA type restrooms in hallway. |  |  |  |  | 2024 |  | N/A | 1 | 1 | 3 | 1.3 | 1 | ls | 1000 | 1000 | PGPC | NO | 2024 |  | 1: 1000
| 717 Erie Boulevard West | Plumbing | Fixtures | Existing drinking fountain not ADA compliant. Provide dual level ADA fountain. |  | PLUMBING FIXTURE |  |  | 2024 |  | N/A | 1 | 1 | 2 | 1.2 | 1 | ls | 7500 | 7500 | PGPC | NO | 2026 |  | 3: 7500
| DeFrancisco Eastwood Community Center | Plumbing | Fixtures | No drinking fountain for facility. Provide dual level ADA fountain. |  |  |  |  | 2024 |  | N/A | 1 | 1 | 2 | 1.2 | 1 | ls | 7500 | 7500 | PGPC | NO | 2026 |  | 3: 7500
| Merrick Head Start | HVAC | Ventilating | Properly tension H&V unit fan belt on north gym H&V unit. |  |  |  |  | 2024 |  | N/A | 1 | 1 | 2 | 1.2 | 1 | ea | 100 | 100 | PGPC | NO | 2025 |  | 2: 100
| Transportation Department | Plumbing | Capital Improvement | Provide ADA accessible restroom. |  |  |  |  | 2024 |  | N/A | 1 | 1 | 1 | 1.1 | 1 | ls | 30000 | 30000 | PGPC | NO | 2026 |  | 3: 30000
| DeFrancisco Eastwood Community Center | HVAC | Energy | Basement AHUs do not have relief air capability for economizer operation which is required per Energy code. Provide relief air ductwork to outdoor louver. |  |  |  |  | 2024 |  | N/A | 1 | 1 | 1 | 1.1 | 1 | ls | 25000 | 25000 | PGPC | NO | 2030 |  | 7: 25000
| Merrick Head Start | Plumbing | Energy | Insulate plumbing piping in basement & crawl space. Test for ACM on original pipe insulation. |  | FLUID LOOP |  |  | 2024 |  | N/A | 1 | 1 | 1 | 1.1 | 1 | ea | 20000 | 20000 | PGPC | NO | 2030 |  | 7: 20000
| Transportation Department | HVAC | Capital Improvement | Provide HVLS destratification fans to improve heating efficiency and circulation in maintenance garage |  |  |  |  | 2024 |  | N/A | 1 | 1 | 1 | 1.1 | 2 | ls | 8500 | 17000 | PGPC | NO | 2030 |  | 7: 17000
| Transportation Department | HVAC | Ventilating | Provide energy recovery ventilator for bus maintenance garage for code required ventilation and to reduce energy consumption. |  |  |  |  | 2024 |  | N/A | 1 | 1 | 1 | 1.1 | 1 | ls | 15000 | 15000 | PGPC | NO | 2030 |  | 7: 15000
| 717 Erie Boulevard West | Electrical | Power | Investigate and add breaker panel to provide additional circuit breaker capacity |  | ELECTRIC PANEL |  |  | 2024 |  | N/A | 1 | 1 | 1 | 1.1 | 1 | ea | 10000 | 10000 | PGPC | NO | 2032 |  | 9: 10000
| Merrick Head Start | HVAC | Energy | Insulate Gymnasium HVAC ductwork |  |  |  |  | 2024 |  | N/A | 1 | 1 | 1 | 1.1 | 1 | ea | 5000 | 5000 | PGPC | NO | 2029 |  | 6: 5000
| Merrick Head Start | HVAC | Energy | Remove abandoned propeller fan and patch wall |  | EXHAUST FAN |  |  | 2024 |  | N/A | 1 | 1 | 1 | 1.1 | 1 | ea | 2200 | 2200 | PGPC | NO | 2030 |  | 7: 2200
| DeFrancisco Eastwood Community Center | Plumbing | Backflow Prevention | No BPV provided for water service. Provide double check backflow preventer per Code. |  | BACKFLOW PREVENTER |  |  | 2024 |  | N/A | 1 | 1 | 1 | 1.1 | 1 | ls | 2000 | 2000 | PGPC | NO | 2025 |  | 2: 2000
| Transportation Department | HVAC | Ventilating | Extend fan discharge for engine exhaust snorkel system up to roof to prevent re-entrainment back into building |  | EXHAUST FAN |  |  | 2024 |  | N/A | 1 | 1 | 1 | 1.1 | 1 | ls | 2000 | 2000 | PGPC | NO | 2025 |  | 2: 2000
| Emma L Johnston Southside Family Resource Center | HVAC | Heating | Check condition of 2nd floor office space for continuity, sealing and sufficient airflow |  |  |  |  | 2024 |  | N/A | 1 | 1 | 1 | 1.1 | 1 | ea | 500 | 500 | PGPC | NO | 2025 |  | 2: 500
| 717 Erie Boulevard West | Plumbing | Energy | Insulate hot water piping from south DHW heater to fixtures per Energy Code. |  | VAV BOX |  |  | 2024 |  | N/A |  |  |  | 0 | 1 | ls | 5000 | 5000 | PGPC | YES | 2025
[9 empty] | 2024 |  | N/A |  |  |  | 0 |  |  |  | 0 | PGPC
[9 empty] | 2024 |  | N/A |  |  |  | 0 |  |  |  | 0 | PGPC
[9 empty] | 2024 |  | N/A |  |  |  | 0 |  |  |  | 0 | PGPC
[9 empty] | 2024 |  | N/A |  |  |  | 0 |  |  |  | 0 | PGPC
[9 empty] | 2024 |  | N/A |  |  |  | 0 |  |  |  | 0 | PGPC
[9 empty] | 2024 |  | N/A |  |  |  | 0 |  |  |  | 0 | PGPC
[9 empty] | 2024 |  | N/A |  |  |  | 0 |  |  |  | 0 | PGPC
[9 empty] | 2024 |  | N/A |  |  |  | 0 |  |  |  | 0 | PGPC
[9 empty] | 2024 |  | N/A |  |  |  | 0 |  |  |  | 0 | PGPC
[9 empty] | 2024 |  | N/A |  |  |  | 0 |  |  |  | 0 | PGPC
[9 empty] | 2024 |  | N/A |  |  |  | 0 |  |  |  | 0 | PGPC
[9 empty] | 2024 |  | N/A |  |  |  | 0 |  |  |  | 0 | PGPC
[9 empty] | 2024 |  | N/A |  |  |  | 0 |  |  |  | 0 | PGPC
[23 empty] | Total by Year | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | Beyond
[22 empty] | 3982750 |  | 155500 | 568250 | 336250 | 577150 | 568300 | 360400 | 779700 | 202900 | 147500 | 86800 | 60000 | 140000
TOTALS FOR DEFICIENCIES NOT COMPLETED AT THIS TIME
[22 empty] | 3982750 |  | 155500 | 568250 | 336250 | 577150 | 568300 | 360400 | 779700 | 202900 | 147500 | 86800 | 60000 | 140000

## Equipment Life Expectancy
ASHRAE service life data: | http://weblegacy.ashrae.org/publicdatabase/
HVACR Equipment Life Expectancy
Equipment Item |  | Median Years
Air conditioners | Window unit | 10
| Residential single or Split Package | 15
| Commercial through-the wall | 15
| Water-cooled package | 15
Heat Pumps | Residential air-to-air | 15
| Commercial air-to-air | 15
| Commercial water-to-air | 19
Roof-top air conditioners | Single-zone | 15
| Multi-zone | 15
Boilers, hot water (steam) | Steel water-tube | 24 (30)
| Steel fire-tube | 25 (25)
| Cast iron | 35 (30)
| Electric | 15
Burners |  | 21
Furnaces | Gas- or oil-fired | 18
Unit heaters | Gas or electric | 13
| Hot water or steam | 20
Radiant Heaters | Electric | 10
| Hot water or steam | 25
Air terminals | Diffusers, grilles, and registers | 27
| Induction and fan coil units | 20
| VAV and double-duct boxes | 20
Air washers |  | 17
Ductwork |  | 30
Dampers |  | 20
Fans | Centrifugal | 25
| Axial | 20
| Propeller | 15
| Ventilating roof-mounted | 20
Coils | DX, water, or steam | 20
| Electric | 15
Heat Exchangers | Shell-and-tube | 24
Reciprocating compressors |  | 20
Packaged chillers | Reciprocating | 20
| Centrifugal | 23
| Absorption | 23
Cooling towers | Galvanized metal | 20
| Wood | 20
| Ceramic | 34
Air-cooled condensers |  | 20
Evaporative condensers |  | 20
Insulation | Molded | 20
| Blanket | 24
Pumps | Base-mounted | 20
| Pipe-mounted | 10
| Sump and well | 10
| Condensate | 15
Reciprocating engines |  | 20
Steam turbines |  | 30
Electric motors |  | 18
Motor starters |  | 17
Electric transformers |  | 30
Controls | Pneumatic | 20
| Electric | 16
| Electronic | 15
Valve actuators | Hydraulic | 15
| Pneumatic | 20
| Self-contained | 10
Domestic Hot Water Heater | Gas | 10
| Electric | 12.5

## Data Fields for Drop Down
| FACILITY | Site | Envelope | Interior | Plumbing | HVAC | Electrical | Elevator | FireSprinkler | FireAlarm | Security | Telcom | Miscellaneous | Other
1 | LaFayette Head Start | Capital Improvement | Capital Improvement | Capital Improvement | Backflow Prevention | Air Conditioning | Capital Improvement | Capital Improvement | Backflow Prevention | Capital Improvement | Capital Improvement | Capital Improvement | ADA
2 | Merrick Head Start | Flatwork / Sidewalks | Insulation | Ceiling | Capital Improvement | Capital Improvement | Energy | General | Capital Improvement | Devices | Devices | General | Capital Improvement
3 | Sumner Head Start & Big Brothers Big Sisters | Landscaping and Appurtenances | Maintenance | Flooring | Domestic HW Heating System | Controls | Interior Lighting | Maintenance | General Piping / Heads | General | General |  | General
4 | County South Family Resource Center | Maintenance | Other | Maintenance | Domestic Water Supply | Energy | Maintenance |  | Main Service | Maintenance | Maintenance |  | Maintenance
5 | Eastside Family Resource Center | Other | Roofing | Other | Energy | Heating | Other |  | Maintenance | Other | Other
6 | Emma L Johnston Southside Family Resource Center | Paving and Curbing | Substructure | Paint | Fixtures | Maintenance | Power |  | Other | Panel | Panel
7 | Westside Family Resource Center | Topology and Drainage | Windows | Wall Condition | Interior Sanitary Drainage | Other | Site Lighting
8 | DeFrancisco Eastwood Community Center | Utilities | Façade |  | Interior Storm drainage | Refrigeration Equipment
9 | Transportation Department |  |  |  | Maintenance | Ventilating
10 | 717 Erie Boulevard West |  |  |  | Natural Gas System
Other
Target Year
| 2024 |  | HVAC | Heating | Piping, systems
| 2025 |  | HVAC | Ventilating | Ductwork, terminals
| 2026 |  | HVAC | Air Conditioning | Piping, systems
| 2027 |  | HVAC | Controls
| 2028 |  | HVAC | Refrigeration Equipment
| 2029 |  | HVAC | Energy | Insulation
| 2030 |  | HVAC | Other
| 2031 |  | Electrical | Power
| 2032 |  | Electrical | Site Lighting
| 2033 |  | Electrical | Interior Lighting
| 2034 |  | Electrical | Energy
| Beyond |  | Electrical | Other
|  |  | Elevator | General
Fire Sprinkler
Fire Sprinkler
Fire Sprinkler
Fire Sprinkler
|  |  | Fire Alarm | General
|  |  | Security | General
|  |  | Telcom | General
|  |  | Miscellaneous | ADA
Other
Cost Source
PGPC
PEACE
Contractor
RSMeans
Manufacturer
Funding Source
Maintenance
Grant
Energy Grant
ADA Improvement
Head Start
Previous Grant sources:
Alyn Foundation
Save The Rain
EQUIPMENT TYPES
| AIR CONDITIONER |  |  | 1
| FIRE ALARM |  |  | 2
| BACKFLOW PREVENTER |  |  | 3
| BOILER, NATURAL GAS |  |  | 4
| BUILDING |  |  | 5
CHILLER
CUSTODIAL EQUIPMENT
COMPACTOR
COMPRESSOR, ALL TYPES
CONDENSER FOR HVAC
COOLER
CONDENSATE RETURN UNIT
NET CONTROLLER
DAMPER
DEHUMIDIFIER
DOMESTIC HOT WATER HEATER ELECTRIC
DOMESTIC HOT WATER HEATER GAS
DOMESTIC HOT WATER PUMP
DOMESTIC HOT WATER HEATER STEAM
DINING AREAS ON CAMPUS
DISHWASHER
DOOR
STORMWATER MANAGEMENT
AIR DRYER COMPRESSED AIR
CLOTHES DRYER
EVAPORATOR
EYEWASH/SAFETY SHOWER
FAN AND COIL UNIT
CIRCULATING FAN
EXHAUST FAN
RETURN FAN
SUPPLY FAN
FILTER
FLOOR DRAIN
FLUID LOOP
FOOD SERVICE ITEMS
FREEZER
FUME HOOD
FURNACE
GENERATOR
HEAT EXCHANGER
HEAT RECOVERY SYSTEM
HEATING AND VENTILATION UNITS
CABINET HEATER
GAS FIRED RADIANT HEATER
HEAT PUMP
HUMIDIFIER
ICE BANK, BEER LINES
ICE MAKER
INDUCTION UNIT
TRUCK LIFT ETC.
EMERGENCY LIGHT
LIGHT POLE
MOTOR
POT MACHINE
PRESSURE REGULATING UNIT
PRESSURE RELIEF VALVE
PACKAGE TERMINAL AC UNIT
PUMP - BOOSTER
PUMP - CIRCULATION
PUMP - CHILLED WATER
PUMP - FIRE
GLYCOL PUMP
PUMP - HOT WATER
JOCKEY PUMP FOR FIRE SPRINKLER
PUMP SUPPLY ALL TYPES
PUMPS - SUMP/SEWAGE
PUMP VACUUM, ALL TYPES
COMPRESSOR RACK
REFRIGERANT CONTAINER
REFRIGERANT TRACKING SYSTEM
REHEAT VAVS
ROOF
CARBON MONOXIDE SENSOR
STAGE LIFT
STEAM STERILIZER
STEAM TRAP
TANK - STORAGE, HOLDING, TRANSFER
COOLING TOWER
TRAY BELT
TURF EQUIPMENT
UNIT HEATER HW&STM
UNIT VENTILATOR
INDUSTRIAL VACUUM
VAV BOX
ALL VEHICLES
VARIABLE SPEED DRIVE
CLOTHES WASHER
ELECTRIC PANEL
PLUMBING FIXTURE
ROOF
ROOF DRAIN
WINDOW